## Organization
COMMUNICATION DOCUMENT ORGANIZATION
MODBUS-TCP
MODBUS ADDRESS
| • | COMMANDS (Bulk Write)
| • | STATUS (Bulk Read)
| • | PARAMETERS
| • | ANALOG CALIBRATION PARAMETERS
| • | NETWORKING PARAMETERS
| • | WARNINGS
| • | ALARMS
| • | HARDWARE DIGITAL INPUTS
| • | HARDWARE ANALOG INPUTS
| • | HARDWARE DIGITAL OUTPUTS
| • | HARDWARE ANALOG OUTPUTS
| • | RAMP/SOAK
| • | HMI DISPLAY VALUES
| • | POWER CONSUMPTION
| • | DATE TIME
| • | SECURITY
MODBUS STATUS DETAILS
MODBUS COMMAND DETAILS
OPC-UA
OBJECTS
| • | COMMANDS
| • | STATUS
| • | PARAMETERS
| • | ANALOG CALIBRATION PARAMETERS
| • | NETWORKING PARAMETERS
| • | WARNINGS
| • | ALARMS
| • | HARDWARE DIGITAL INPUTS
| • | HARDWARE ANALOG INPUTS
| • | HARDWARE DIGITAL OUTPUTS
| • | HARDWARE ANALOG OUTPUTS
| • | RAMP/SOAK
| • | HMI DISPLAY VALUES
| • | POWER CONSUMPTION
| • | DATE TIME
METHODS -- See MODBUS COMMAND DETAILS
SPI
SPI OPTION PARAMETERS
SPI STATUS WORD
SPI MACHINE WORD 1
SPI MACHINE WORD 2
SPI PROTOCOL v4.00 (for reference)
EUROMAP
EUROMAP
EUROMAP ALARMS
EUROMAP UNIT OF MEASURE
EUROMAP SECURITY
EUROMAP 82.1 v1.01 (for reference)
EUROMAP 83 v1.03 (for reference)

## SPI
SPI OPTION PARAMETERS
COMMAND | POLL | SELECT | DESCRIPTION | LINKED TAG
Echo | 0x20 0x21 | 0x20 0x20 | Controller integrity command used to accept and retain data and provide it in response to a poll inuiry in an open 4-byte ASCII format with ASCII units.
Version |  | 0x20 0x22 | Controller version command used to provide a version number following format: AABB, where AA=SPI assigned version level, BB=vendor assigned version level in an open 4-byte ASCII format with ASCII units. | r_PAR_SoftwareVersion.CurrentValue
Set Point Process Temperature | 0x20 0x31 | 0x20 0x30 | Target supply coolant temperature leaving the unit in a numeric format in °F. | r_HD_EffectiveSetpoint.Value
Alarm, High Temperature Deviation | 0x20 0x33 | 0x20 0x32 | Value in conjunction with the process set point that determines the high alarm temperature in a numberic format in °F must always be positive. | r_PAR_TempDev_OverSP.CurrentValue
Alarm, Low Temperature Deviation | 0x20 0x35 | 0x20 0x34 | Value in conjunction with the process set point that determines the high alarm temperature in a numberic format in °F must always be positive. | r_PAR_TempDev_UnderSP.CurrentValue
Status, Process |  | 0x20 0x40 | See "SPI Status Word" for details.
Status, Machine 1 |  | 0x20 0x42 | See "SPI Machine Word 1" for details.
Status, Machine 2 |  | 0x20 0x44 | See "SPI Machine Word 2" for details.
Mode, Machine | 0x20 0x49 | 0x20 0x48 | Machine mode in two 8-bit bytes. When polling 20 48 bit 0 indicated the machine is off. 20 40 bit 0 commands the unit to be turned on or off (on when high or off when low). 20 40 bit 1 is used to recognize the alarm condition.
Temperature, To Process (Supply) |  | 0x20 0x70 | Returns the process supply temperature in a numeric format in °F.
Temperature, To Process (Return) |  | 0x20 0x72 | Returns the process return temperature in a numeric format in °F.
* NOTE: both High and Low Temperature Deviation commands set the same variable. Use only one of these commands to avoid problems
See SPI Status Words for status words and BIT positions for Process Status, Machine 1 Status, and Machine 2 status. For more information on the SPI protocol, you can obtain the SPI Communication Protocol Manual by contacting: The Society of the Plastics Industry, Inc. 1801 K Street, NW Suite 600K Washington, DC 20006 (202) 974-5200 Fac: (202) 296-7005 www.plasticsindustry.org

## SPI Status Word
SPI STATUS WORD
STATUS BIT | CONDITION | LINKED TAGS or LOGICAL DERRIVATION
0.0 | System Processing | b_TCU_IsOperational
0.1 | Alarm - Process | Status bit 0.2 OR 0.3 is set.
0.2 | Alarm - Machine | Status bit 0.4 OR 0.5 is set.
0.3 | Alarm - System | Status bit 0.7 OR 0.9 OR 0.15 is set, OR there is a b_ProbeFailure, where b_ProbeFailure= (((r_IN_SupplyRTD.Implemented) AND (r_IN_SupplyRTD.Error <> 10)) OR ((r_IN_ReturnRTD.Implemented) AND (r_IN_ReturnRTD.Error <> 10)) OR ((r_IN_RemoteRTD.Implemented) AND (r_IN_RemoteRTD.Error <> 10)) OR ((r_IN_AnalogProcess.Implemented) AND (r_IN_AnalogProcess.Error <> 10)) OR ((r_NET_ProcessValueTemperature.Implemented) AND (r_NET_ProcessValueTemperature.Error <> 10)) OR ((r_IN_ReturnPressure.Implemented) AND (r_IN_ReturnPressure.Error <> 10)) OR ((r_IN_SupplyPressure.Implemented) AND (r_IN_SupplyPressure.Error <> 10)) OR ((r_IN_AnalogFlowmeter.Implemented) AND (r_IN_AnalogFlowmeter.Error <> 10)) OR (b_WRN_FO_SupToRet_SupRTD_Open.Enable AND b_WRN_FO_SupToRet_SupRTD_Open.Value) OR (b_WRN_FO_SupToRet_SupRTD_Shorted.Enable AND b_WRN_FO_SupToRet_SupRTD_Shorted.Value) OR (b_WRN_FO_SupToRet_SupRTD_Other.Enable AND b_WRN_FO_SupToRet_SupRTD_Other.Value) OR (b_WRN_FO_RetToSup_RetRTD_Open.Enable AND b_WRN_FO_RetToSup_RetRTD_Open.Value) OR (b_WRN_FO_RetToSup_RetRTD_Shorted.Enable AND b_WRN_FO_RetToSup_RetRTD_Shorted.Value) OR (b_WRN_FO_RetToSup_RetRTD_Other.Enable AND b_WRN_FO_RetToSup_RetRTD_Other.Value) OR (b_WRN_FO_RemToRet_RemRTD_Open.Enable AND b_WRN_FO_RemToRet_RemRTD_Open.Value) OR (b_WRN_FO_RemToRet_RemRTD_Shorted.Enable AND b_WRN_FO_RemToRet_RemRTD_Shorted.Value) OR (b_WRN_FO_RemToRet_RemRTD_Other.Enable AND b_WRN_FO_RemToRet_RemRTD_Other.Value) OR (b_WRN_FO_AnaToRet_AnaProcInHigh.Enable AND b_WRN_FO_AnaToRet_AnaProcInHigh.Value) OR (b_WRN_FO_AnaToRet_AnaProcInLow.Enable AND b_WRN_FO_AnaToRet_AnaProcInLow.Value) OR (b_WRN_FO_AnaToRet_AnaProcInOther.Enable AND b_WRN_FO_AnaToRet_AnaProcInOther.Value) OR (b_WRN_FO_NetToRet_NetProcHigh.Enable AND b_WRN_FO_NetToRet_NetProcHigh.Value) OR (b_WRN_FO_NetToRet_NetProcLow.Enable AND b_WRN_FO_NetToRet_NetProcLow.Value) OR (b_WRN_FO_NetToRet_NetProcHB.Enable AND b_WRN_FO_NetToRet_NetProcHB.Value) OR (b_WRN_SupplyTransducerHigh.Enable AND b_WRN_SupplyTransducerHigh.Value) OR (b_WRN_SupplyTransducerLow.Enable AND b_WRN_SupplyTransducerLow.Value) OR (b_WRN_SupplyTransducerOther.Enable AND b_WRN_SupplyTransducerOther.Value) OR (b_WRN_SupplyRTD_Open.Enable AND b_WRN_SupplyRTD_Open.Value) OR (b_WRN_SupplyRTD_Shorted.Enable AND b_WRN_SupplyRTD_Shorted.Value) OR (b_WRN_SupplyRTD_Other.Enable AND b_WRN_SupplyRTD_Other.Value) OR (b_WRN_ReturnRTD_Open.Enable AND b_WRN_ReturnRTD_Open.Value) OR (b_WRN_ReturnRTD_Shorted.Enable AND b_WRN_ReturnRTD_Shorted.Value) OR (b_WRN_ReturnRTD_Other.Enable AND b_WRN_ReturnRTD_Other.Value) OR (b_WRN_AnaFlowmeterHigh.Enable AND b_WRN_AnaFlowmeterHigh.Value) OR (b_WRN_AnaFlowmeterLow.Enable AND b_WRN_AnaFlowmeterLow.Value) OR (b_WRN_AnaFlowmeterOther.Enable AND b_WRN_AnaFlowmeterOther.Value) OR (b_ALM_SupplyRTD_Open.Enable AND b_ALM_SupplyRTD_Open.Value) OR (b_ALM_SupplyRTD_Shorted.Enable AND b_ALM_SupplyRTD_Shorted.Value) OR (b_ALM_SupplyRTD_Other.Enable AND b_ALM_SupplyRTD_Other.Value) OR (b_ALM_ReturnRTD_Open.Enable AND b_ALM_ReturnRTD_Open.Value) OR (b_ALM_ReturnRTD_Shorted.Enable AND b_ALM_ReturnRTD_Shorted.Value) OR (b_ALM_ReturnRTD_Other.Enable AND b_ALM_ReturnRTD_Other.Value) OR (b_ALM_RemoteRTD_Open.Enable AND b_ALM_RemoteRTD_Open.Value) OR (b_ALM_RemoteRTD_Shorted.Enable AND b_ALM_RemoteRTD_Shorted.Value) OR (b_ALM_RemoteRTD_Other.Enable AND b_ALM_RemoteRTD_Other.Value) OR (b_ALM_AnaProcInHigh.Enable AND b_ALM_AnaProcInHigh.Value) OR (b_ALM_AnaProcInLow.Enable AND b_ALM_AnaProcInLow.Value) OR (b_ALM_AnaProcInOther.Enable AND b_ALM_AnaProcInOther.Value) OR (b_ALM_NetProcHigh.Enable AND b_ALM_NetProcHigh.Value) OR (b_ALM_NetProcLow.Enable AND b_ALM_NetProcLow.Value) OR (b_ALM_NetProcHeartbeat.Enable AND b_ALM_NetProcHeartbeat.Value) OR (b_ALM_ReturnTransducerHigh.Enable AND b_ALM_ReturnTransducerHigh.Value) OR (b_ALM_ReturnTransducerLow.Enable AND b_ALM_ReturnTransducerLow.Value) OR (b_ALM_ReturnTransducerOther.Enable AND b_ALM_ReturnTransducerOther.Value) OR (b_ALM_SupplyTransducerHigh.Enable AND b_ALM_SupplyTransducerHigh.Value) OR (b_ALM_SupplyTransducerLow.Enable AND b_ALM_SupplyTransducerLow.Value) OR (b_ALM_SupplyTransducerOther.Enable AND b_ALM_SupplyTransducerOther.Value) OR (b_ALM_AnaFlowmeterHigh.Enable AND b_ALM_AnaFlowmeterHigh.Value) OR (b_ALM_AnaFlowmeterLow.Enable AND b_ALM_AnaFlowmeterLow.Value) OR (b_ALM_AnaFlowmeterOther.Enable AND b_ALM_AnaFlowmeterOther.Value))
0.4 | High Deviation | ((b_WRN_HighDeviation.Enable AND b_WRN_HighDeviation.Value) OR (b_ALM_HighDeviation.Enable AND b_ALM_HighDeviation.Value))
0.5 | Low Deviation | ((b_WRN_LowDeviation.Enable AND b_WRN_LowDeviation.Value) OR (b_ALM_LowDeviation.Enable AND b_ALM_LowDeviation.Value))
0.6 | High Pressure | ((b_ALM_PressureTooHigh.Enable AND b_ALM_PressureTooHigh.Value))
0.7 | Low Pressure | ((b_WRN_PressureBelowMinimum.Enable AND b_WRN_PressureBelowMinimum.Value) OR (b_WRN_PressureNotHighEnough.Enable AND b_WRN_PressureNotHighEnough.Value) OR (b_WRN_SetpointTooHighForPressure.Enable AND b_WRN_SetpointTooHighForPressure.Value) OR (b_ALM_LowPressureStandbyTimeout.Enable AND b_ALM_LowPressureStandbyTimeout.Value) OR (b_ALM_LowPressureStrikeout.Enable AND b_ALM_LowPressureStrikeout.Value) OR (b_ALM_PressureBelowMinimum.Enable AND b_ALM_PressureBelowMinimum.Value) OR (b_ALM_PressureNotHighEnough.Enable AND b_ALM_PressureNotHighEnough.Value) OR (b_ALM_RampSoakPaused.Enable AND b_ALM_RampSoakPaused.Value) OR (e_MSM_State.LP))
0.8 | Spare - Reserved | Always FALSE.
0.9 | Alarm - Low Flow | ((b_WRN_FlowmeterLowFlow.Enable AND b_WRN_FlowmeterLowFlow.Value) OR ( b_ALM_FlowmeterLowFlow.Enable AND b_ALM_FlowmeterLowFlow.Value))
0.10 | Spare - Reserved | Always FALSE.
0.11 | Spare - Reserved | Always FALSE.
0.12 | Spare - Reserved | Always FALSE.
0.13 | Spare - Reserved | Always FALSE.
0.14 | Spare - Open | Always FALSE.
0.15 | Pump | ((b_WRN_PumpOverload.Enable AND b_WRN_PumpOverload.Value) OR (b_ALM_PumpOverload.Enable AND b_ALM_PumpOverload.Value))
NOTES: 1. If a bit is not shown to be SET, then it is cleared. 2. The SPI I/O list defines the Processing bit as being cleared if the unit is not processing, else it is SET. 3. System Alarm bit is SET if an alarm is present. It is the logical OR of Process alarm and Machine alarm. 4. Processing, System Alarm, Process Alarm, Machine Alarm bits are repeated for STATUS, MACHINE-1, MACHINE-2 status words.

## SPI Machine Word 1
SPI MACHINE WORD 1
STATUS BIT | CONDITION | LINKED TAGS or LOGICAL DERRIVATION
0.0 | System Processing | b_TCU_IsOperational
0.1 | Alarm - System | Status bit 0.2 OR 0.3 is set.
0.2 | Alarm - Process | ((b_ALM_UserTempHigh.Enable AND b_ALM_UserTempHigh.Value) OR (b_ALM_UserTempLow.Enable AND b_ALM_UserTempLow.Value))
0.3 | Alarm - Machine | ((b_ALM_FactoryTempHigh.Enable AND b_ALM_FactoryTempHigh.Value) OR (b_ALM_FactoryTempLow.Enable AND b_ALM_FactoryTempLow.Value) OR (b_WRN_PumpOverload.Enable AND b_WRN_PumpOverload.Value) OR (b_ALM_PumpOverload.Enable AND b_ALM_PumpOverload.Value) OR (b_ALM_PhaseMonitor.Enable AND b_ALM_PhaseMonitor.Value) OR (b_ALM_FlowmeterLowFlow.Enable AND b_ALM_FlowmeterLowFlow.Value) OR (b_WRN_FlowmeterLowFlow.Enable AND b_WRN_FlowmeterLowFlow.Value) OR (b_ProbeFailure)), where b_ProbeFailure= (((r_IN_SupplyRTD.Implemented) AND (r_IN_SupplyRTD.Error <> 10)) OR ((r_IN_ReturnRTD.Implemented) AND (r_IN_ReturnRTD.Error <> 10)) OR ((r_IN_RemoteRTD.Implemented) AND (r_IN_RemoteRTD.Error <> 10)) OR ((r_IN_AnalogProcess.Implemented) AND (r_IN_AnalogProcess.Error <> 10)) OR ((r_NET_ProcessValueTemperature.Implemented) AND (r_NET_ProcessValueTemperature.Error <> 10)) OR ((r_IN_ReturnPressure.Implemented) AND (r_IN_ReturnPressure.Error <> 10)) OR ((r_IN_SupplyPressure.Implemented) AND (r_IN_SupplyPressure.Error <> 10)) OR ((r_IN_AnalogFlowmeter.Implemented) AND (r_IN_AnalogFlowmeter.Error <> 10)) OR (b_WRN_FO_SupToRet_SupRTD_Open.Enable AND b_WRN_FO_SupToRet_SupRTD_Open.Value) OR (b_WRN_FO_SupToRet_SupRTD_Shorted.Enable AND b_WRN_FO_SupToRet_SupRTD_Shorted.Value) OR (b_WRN_FO_SupToRet_SupRTD_Other.Enable AND b_WRN_FO_SupToRet_SupRTD_Other.Value) OR (b_WRN_FO_RetToSup_RetRTD_Open.Enable AND b_WRN_FO_RetToSup_RetRTD_Open.Value) OR (b_WRN_FO_RetToSup_RetRTD_Shorted.Enable AND b_WRN_FO_RetToSup_RetRTD_Shorted.Value) OR (b_WRN_FO_RetToSup_RetRTD_Other.Enable AND b_WRN_FO_RetToSup_RetRTD_Other.Value) OR (b_WRN_FO_RemToRet_RemRTD_Open.Enable AND b_WRN_FO_RemToRet_RemRTD_Open.Value) OR (b_WRN_FO_RemToRet_RemRTD_Shorted.Enable AND b_WRN_FO_RemToRet_RemRTD_Shorted.Value) OR (b_WRN_FO_RemToRet_RemRTD_Other.Enable AND b_WRN_FO_RemToRet_RemRTD_Other.Value) OR (b_WRN_FO_AnaToRet_AnaProcInHigh.Enable AND b_WRN_FO_AnaToRet_AnaProcInHigh.Value) OR (b_WRN_FO_AnaToRet_AnaProcInLow.Enable AND b_WRN_FO_AnaToRet_AnaProcInLow.Value) OR (b_WRN_FO_AnaToRet_AnaProcInOther.Enable AND b_WRN_FO_AnaToRet_AnaProcInOther.Value) OR (b_WRN_FO_NetToRet_NetProcHigh.Enable AND b_WRN_FO_NetToRet_NetProcHigh.Value) OR (b_WRN_FO_NetToRet_NetProcLow.Enable AND b_WRN_FO_NetToRet_NetProcLow.Value) OR (b_WRN_FO_NetToRet_NetProcHB.Enable AND b_WRN_FO_NetToRet_NetProcHB.Value) OR (b_WRN_SupplyTransducerHigh.Enable AND b_WRN_SupplyTransducerHigh.Value) OR (b_WRN_SupplyTransducerLow.Enable AND b_WRN_SupplyTransducerLow.Value) OR (b_WRN_SupplyTransducerOther.Enable AND b_WRN_SupplyTransducerOther.Value) OR (b_WRN_SupplyRTD_Open.Enable AND b_WRN_SupplyRTD_Open.Value) OR (b_WRN_SupplyRTD_Shorted.Enable AND b_WRN_SupplyRTD_Shorted.Value) OR (b_WRN_SupplyRTD_Other.Enable AND b_WRN_SupplyRTD_Other.Value) OR (b_WRN_ReturnRTD_Open.Enable AND b_WRN_ReturnRTD_Open.Value) OR (b_WRN_ReturnRTD_Shorted.Enable AND b_WRN_ReturnRTD_Shorted.Value) OR (b_WRN_ReturnRTD_Other.Enable AND b_WRN_ReturnRTD_Other.Value) OR (b_WRN_AnaFlowmeterHigh.Enable AND b_WRN_AnaFlowmeterHigh.Value) OR (b_WRN_AnaFlowmeterLow.Enable AND b_WRN_AnaFlowmeterLow.Value) OR (b_WRN_AnaFlowmeterOther.Enable AND b_WRN_AnaFlowmeterOther.Value) OR (b_ALM_SupplyRTD_Open.Enable AND b_ALM_SupplyRTD_Open.Value) OR (b_ALM_SupplyRTD_Shorted.Enable AND b_ALM_SupplyRTD_Shorted.Value) OR (b_ALM_SupplyRTD_Other.Enable AND b_ALM_SupplyRTD_Other.Value) OR (b_ALM_ReturnRTD_Open.Enable AND b_ALM_ReturnRTD_Open.Value) OR (b_ALM_ReturnRTD_Shorted.Enable AND b_ALM_ReturnRTD_Shorted.Value) OR (b_ALM_ReturnRTD_Other.Enable AND b_ALM_ReturnRTD_Other.Value) OR (b_ALM_RemoteRTD_Open.Enable AND b_ALM_RemoteRTD_Open.Value) OR (b_ALM_RemoteRTD_Shorted.Enable AND b_ALM_RemoteRTD_Shorted.Value) OR (b_ALM_RemoteRTD_Other.Enable AND b_ALM_RemoteRTD_Other.Value) OR (b_ALM_AnaProcInHigh.Enable AND b_ALM_AnaProcInHigh.Value) OR (b_ALM_AnaProcInLow.Enable AND b_ALM_AnaProcInLow.Value) OR (b_ALM_AnaProcInOther.Enable AND b_ALM_AnaProcInOther.Value) OR (b_ALM_NetProcHigh.Enable AND b_ALM_NetProcHigh.Value) OR (b_ALM_NetProcLow.Enable AND b_ALM_NetProcLow.Value) OR (b_ALM_NetProcHeartbeat.Enable AND b_ALM_NetProcHeartbeat.Value) OR (b_ALM_ReturnTransducerHigh.Enable AND b_ALM_ReturnTransducerHigh.Value) OR (b_ALM_ReturnTransducerLow.Enable AND b_ALM_ReturnTransducerLow.Value) OR (b_ALM_ReturnTransducerOther.Enable AND b_ALM_ReturnTransducerOther.Value) OR (b_ALM_SupplyTransducerHigh.Enable AND b_ALM_SupplyTransducerHigh.Value) OR (b_ALM_SupplyTransducerLow.Enable AND b_ALM_SupplyTransducerLow.Value) OR (b_ALM_SupplyTransducerOther.Enable AND b_ALM_SupplyTransducerOther.Value) OR (b_ALM_AnaFlowmeterHigh.Enable AND b_ALM_AnaFlowmeterHigh.Value) OR (b_ALM_AnaFlowmeterLow.Enable AND b_ALM_AnaFlowmeterLow.Value) OR (b_ALM_AnaFlowmeterOther.Enable AND b_ALM_AnaFlowmeterOther.Value))
0.4 | Alarm - High Temp Limit | ((b_ALM_FactoryTempHigh.Enable AND b_ALM_FactoryTempHigh.Value) OR (b_ALM_UserTempHigh.Enable AND b_ALM_UserTempHigh.Value))
0.5 | Alarm - Low Temp Limit | ((b_ALM_FactoryTempLow.Enable AND b_ALM_FactoryTempLow.Value) OR (b_ALM_UserTempLow.Enable AND b_ALM_UserTempLow.Value))
0.6 | Spare | Always FALSE.
0.7 | Spare | Always FALSE.
0.8 | Spare | Always FALSE.
0.9 | Spare | Always FALSE.
0.10 | Spare | Always FALSE.
0.11 | Spare | Always FALSE.
0.12 | Spare | Always FALSE.
0.13 | Spare | Always FALSE.
0.14 | Alarm - Phase Monitor | b_ALM_PhaseMonitor.Enable AND b_ALM_PhaseMonitor.Value
0.15 | Alarm - Pump | ((b_WRN_PumpOverload.Enable AND b_WRN_PumpOverload.Value) OR (b_ALM_PumpOverload.Enable AND b_ALM_PumpOverload.Value))
NOTES: 1. If a bit is not shown to be SET, then it is cleared. 2. The SPI I/O list defines the Processing bit as being cleared if the unit is not processing, else it is SET. 3. System Alarm bit is SET if an alarm is present. It is the logical OR of Process alarm and Machine alarm. 4. Processing, System Alarm, Process Alarm, Machine Alarm bits are repeated for STATUS, MACHINE-1, MACHINE-2 status words.

## SPI Machine Word 2
SPI MACHINE WORD 2
STATUS BIT | CONDITION | LINKED TAGS or LOGICAL DERRIVATION
0.0 | System Processing | b_TCU_IsOperational
0.1 | Alarm - System | Status bit 0.2 OR 0.3 is set.
0.2 | Alarm - Process | Status bit 0.4 OR 0.5 is set, OR (b_ALM_Brownout.Enable AND b_ALM_Brownout.Value))
0.3 | Alarm - Machine | ((Machine Word 2, bit 0.4 is set) OR (Machine Word 2, bit 0.11 is set) OR (Machine Word 2, bit 0.12 is set) OR (Machine Word 2, bit 0.13 is set) OR (Machine Word 2, bit 0.14 is set) OR (Machine Word 2, bit 0.15 is set) OR (Machine Word 1, bit 0.15 is set) OR (Status bit 0.7 is set) OR (Status bit 0.9 is set) OR (Status bit 0.15 is set))
0.4 | Sensor Failure | (((r_IN_SupplyRTD.Implemented) AND (r_IN_SupplyRTD.Error <> 10)) OR ((r_IN_ReturnRTD.Implemented) AND (r_IN_ReturnRTD.Error <> 10)) OR ((r_IN_RemoteRTD.Implemented) AND (r_IN_RemoteRTD.Error <> 10)) OR ((r_IN_AnalogProcess.Implemented) AND (r_IN_AnalogProcess.Error <> 10)) OR ((r_NET_ProcessValueTemperature.Implemented) AND (r_NET_ProcessValueTemperature.Error <> 10)) OR ((r_IN_ReturnPressure.Implemented) AND (r_IN_ReturnPressure.Error <> 10)) OR ((r_IN_SupplyPressure.Implemented) AND (r_IN_SupplyPressure.Error <> 10)) OR ((r_IN_AnalogFlowmeter.Implemented) AND (r_IN_AnalogFlowmeter.Error <> 10)) OR (b_WRN_FO_SupToRet_SupRTD_Open.Enable AND b_WRN_FO_SupToRet_SupRTD_Open.Value) OR (b_WRN_FO_SupToRet_SupRTD_Shorted.Enable AND b_WRN_FO_SupToRet_SupRTD_Shorted.Value) OR (b_WRN_FO_SupToRet_SupRTD_Other.Enable AND b_WRN_FO_SupToRet_SupRTD_Other.Value) OR (b_WRN_FO_RetToSup_RetRTD_Open.Enable AND b_WRN_FO_RetToSup_RetRTD_Open.Value) OR (b_WRN_FO_RetToSup_RetRTD_Shorted.Enable AND b_WRN_FO_RetToSup_RetRTD_Shorted.Value) OR (b_WRN_FO_RetToSup_RetRTD_Other.Enable AND b_WRN_FO_RetToSup_RetRTD_Other.Value) OR (b_WRN_FO_RemToRet_RemRTD_Open.Enable AND b_WRN_FO_RemToRet_RemRTD_Open.Value) OR (b_WRN_FO_RemToRet_RemRTD_Shorted.Enable AND b_WRN_FO_RemToRet_RemRTD_Shorted.Value) OR (b_WRN_FO_RemToRet_RemRTD_Other.Enable AND b_WRN_FO_RemToRet_RemRTD_Other.Value) OR (b_WRN_FO_AnaToRet_AnaProcInHigh.Enable AND b_WRN_FO_AnaToRet_AnaProcInHigh.Value) OR (b_WRN_FO_AnaToRet_AnaProcInLow.Enable AND b_WRN_FO_AnaToRet_AnaProcInLow.Value) OR (b_WRN_FO_AnaToRet_AnaProcInOther.Enable AND b_WRN_FO_AnaToRet_AnaProcInOther.Value) OR (b_WRN_FO_NetToRet_NetProcHigh.Enable AND b_WRN_FO_NetToRet_NetProcHigh.Value) OR (b_WRN_FO_NetToRet_NetProcLow.Enable AND b_WRN_FO_NetToRet_NetProcLow.Value) OR (b_WRN_FO_NetToRet_NetProcHB.Enable AND b_WRN_FO_NetToRet_NetProcHB.Value) OR (b_WRN_SupplyTransducerHigh.Enable AND b_WRN_SupplyTransducerHigh.Value) OR (b_WRN_SupplyTransducerLow.Enable AND b_WRN_SupplyTransducerLow.Value) OR (b_WRN_SupplyTransducerOther.Enable AND b_WRN_SupplyTransducerOther.Value) OR (b_WRN_SupplyRTD_Open.Enable AND b_WRN_SupplyRTD_Open.Value) OR (b_WRN_SupplyRTD_Shorted.Enable AND b_WRN_SupplyRTD_Shorted.Value) OR (b_WRN_SupplyRTD_Other.Enable AND b_WRN_SupplyRTD_Other.Value) OR (b_WRN_ReturnRTD_Open.Enable AND b_WRN_ReturnRTD_Open.Value) OR (b_WRN_ReturnRTD_Shorted.Enable AND b_WRN_ReturnRTD_Shorted.Value) OR (b_WRN_ReturnRTD_Other.Enable AND b_WRN_ReturnRTD_Other.Value) OR (b_WRN_AnaFlowmeterHigh.Enable AND b_WRN_AnaFlowmeterHigh.Value) OR (b_WRN_AnaFlowmeterLow.Enable AND b_WRN_AnaFlowmeterLow.Value) OR (b_WRN_AnaFlowmeterOther.Enable AND b_WRN_AnaFlowmeterOther.Value) OR (b_ALM_SupplyRTD_Open.Enable AND b_ALM_SupplyRTD_Open.Value) OR (b_ALM_SupplyRTD_Shorted.Enable AND b_ALM_SupplyRTD_Shorted.Value) OR (b_ALM_SupplyRTD_Other.Enable AND b_ALM_SupplyRTD_Other.Value) OR (b_ALM_ReturnRTD_Open.Enable AND b_ALM_ReturnRTD_Open.Value) OR (b_ALM_ReturnRTD_Shorted.Enable AND b_ALM_ReturnRTD_Shorted.Value) OR (b_ALM_ReturnRTD_Other.Enable AND b_ALM_ReturnRTD_Other.Value) OR (b_ALM_RemoteRTD_Open.Enable AND b_ALM_RemoteRTD_Open.Value) OR (b_ALM_RemoteRTD_Shorted.Enable AND b_ALM_RemoteRTD_Shorted.Value) OR (b_ALM_RemoteRTD_Other.Enable AND b_ALM_RemoteRTD_Other.Value) OR (b_ALM_AnaProcInHigh.Enable AND b_ALM_AnaProcInHigh.Value) OR (b_ALM_AnaProcInLow.Enable AND b_ALM_AnaProcInLow.Value) OR (b_ALM_AnaProcInOther.Enable AND b_ALM_AnaProcInOther.Value) OR (b_ALM_NetProcHigh.Enable AND b_ALM_NetProcHigh.Value) OR (b_ALM_NetProcLow.Enable AND b_ALM_NetProcLow.Value) OR (b_ALM_NetProcHeartbeat.Enable AND b_ALM_NetProcHeartbeat.Value) OR (b_ALM_ReturnTransducerHigh.Enable AND b_ALM_ReturnTransducerHigh.Value) OR (b_ALM_ReturnTransducerLow.Enable AND b_ALM_ReturnTransducerLow.Value) OR (b_ALM_ReturnTransducerOther.Enable AND b_ALM_ReturnTransducerOther.Value) OR (b_ALM_SupplyTransducerHigh.Enable AND b_ALM_SupplyTransducerHigh.Value) OR (b_ALM_SupplyTransducerLow.Enable AND b_ALM_SupplyTransducerLow.Value) OR (b_ALM_SupplyTransducerOther.Enable AND b_ALM_SupplyTransducerOther.Value) OR (b_ALM_AnaFlowmeterHigh.Enable AND b_ALM_AnaFlowmeterHigh.Value) OR (b_ALM_AnaFlowmeterLow.Enable AND b_ALM_AnaFlowmeterLow.Value) OR (b_ALM_AnaFlowmeterOther.Enable AND b_ALM_AnaFlowmeterOther.Value))
0.5 | Spare | Always FALSE.
0.6 | Spare | Always FALSE.
0.7 | Spare | Always FALSE.
0.8 | Spare | Always FALSE.
0.9 | Resistance Control | Always FALSE. Intended purpose in SPI spec is unknown.
0.10 | Brownout | b_ALM_Brownout.Enable AND b_ALM_Brownout.Value
0.11 | Hardwire Overtemp | (((b_IN_HeaterHighTemp.Implemented) AND (NOT b_IN_HeaterHighTemp.Value)) OR (b_ALM_Overtemperature.Enable AND b_ALM_Overtemperature.Value))
0.12 | Electrical Panel Too Hot | (b_ALM_ElecPanelTooHot.Enable AND b_ALM_ElecPanelTooHot.Value);
0.13 | Heater Contactor Malfunction | ((b_ALM_HeaterContactorStuckClosed.Enable AND b_ALM_HeaterContactorStuckClosed.Value) OR (b_ALM_HeaterContactorStuckOpen.Enable AND b_ALM_HeaterContactorStuckOpen.Value))
0.14 | High Temperature | ((b_ALM_ElecPanelTooHot.Enable AND b_ALM_ElecPanelTooHot.Value) OR (b_ALM_HeaterContactorStuckClosed.Enable AND b_ALM_HeaterContactorStuckClosed.Value) OR ((b_IN_HeaterHighTemp.Implemented) AND (NOT b_IN_HeaterHighTemp.Value)) OR (b_ALM_Overtemperature.Enable AND b_ALM_Overtemperature.Value))
0.15 | Low Temperature | b_ALM_HeaterContactorStuckOpen.Enable AND b_ALM_HeaterContactorStuckOpen.Value
NOTES: 1. If a bit is not shown to be SET, then it is cleared. 2 . The SPI I/O list defines the Processing bit as being cleared if the unit is not processing, else it is SET. 3. System Alarm bit is SET if an alarm is present. It is the logical OR of Process alarm and Machine alarm. 4. Processing, System Alarm, Process Alarm, Machine Alarm bits are repeated for STATUS, MACHINE-1, MACHINE-2 status words.

## Modbus Address
MODBUS DEFINITION
| ENABLED | ACCESS TYPE | ADDRESS | INTERNAL TAG NAME | SIZE (WORDS) | DATATYPE | COMMENTS | UNITS
Frequently-written commands, intended for bulk write.
| NO | Holding Register | 1000 | r_NET_Cmd_ProcValueTemp | 2 | Floating point | Not currently enabled. | °C
| NO | Holding Register | 1002 | r_NET_Cmd_SetpointTemperature | 2 | Floating point | Not currently enabled. | °C
| YES | Holding Register | 1004 | w_NET_Cmd_MachineState | 2 | Bit-packed word | See Modbus_Command sheet for details. | N/A
| NO | Holding Register | 1006 | w_NET_Cmd_ProcessValueState | 1 | Bit-packed word | See Modbus_Command sheet for details, but not currently enabled. | N/A
| YES | Holding Register | 1007 | w_NET_Cmd_SetpointState | 2 | Bit/Byte-packed word | See Modbus_Command sheet for details. | N/A
| YES | Holding Register | 1009 | w_NET_Cmd_UserInteraction | 1 | Bit-packed word | See Modbus_Command sheet for details. | N/A
| YES | Holding Register | 1010 | w_NET_NetworkState | 1 | Bit/Byte-packed word | See Modbus_Command sheet for details. | N/A
| NO | Holding Register | 1011 | w_NET_BankedScheduledPollingInterval_ms | 1 | Integer |  | ms
| NO | Holding Register | 1012 | w_NET_BankedUnitAssignment | 1 | Bit/Byte-packed word | See Modbus_Command sheet for details. | N/A
Frequently-read status, intended for bulk read.
| YES | Input Register | 1000 | w_NET_MSM_TSM_State | 1 | Byte-packed word | See Modbus_Status sheet for details (byte enumeration). | <enumeration>
| YES | Input Register | 1001 | r_NET_ProcessValueTemperature.CurrentValue | 2 | Floating point | See Modbus_Status sheet for details. | °C
| YES | Input Register | 1003 | r_NET_SetpointTemperature.CurrentValue | 2 | Floating point | See Modbus_Status sheet for details. | °C
| YES | Input Register | 1005 | r_NET_Sts_ProcValueTemperature | 2 | Floating point | See Modbus_Status sheet for details. | °C
| YES | Input Register | 1007 | r_NET_Sts_SetpointTemperature | 2 | Floating point | See Modbus_Status sheet for details. | °C
| YES | Input Register | 1009 | w_NET_Sts_CountdownState | 1 | Byte-packed word | See Modbus_Status sheet for details (byte enumeration). | <enumeration>
| YES | Input Register | 1010 | w_NET_Sts_CountdownTimer | 1 | Integer | See Modbus_Status sheet for details (word). | seconds
| YES | Input Register | 1011 | w_NET_Sts_MachineState | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | <enumeration>
| YES | Input Register | 1013 | w_NET_Sts_ProcessValueState | 2 | Bit-packed word | See Modbus_Status sheet for details (byte enumeration and bit-packed). | <enumeration>
| YES | Input Register | 1015 | w_NET_Sts_SetpointState | 2 | Bit/Byte-packed word | See Modbus_Status sheet for details (byte enumeration and bit-packed). | <enumeration>
| YES | Input Register | 1017 | w_NET_Sts_TemperatureState | 2 | Bit/Byte-packed word | See Modbus_Status sheet for details (bit-packed, and byte value). | <enumeration>
| YES | Input Register | 1019 | w_NET_Sts_AlarmMap1 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1021 | w_NET_Sts_AlarmMap2 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1023 | w_NET_Sts_AlarmMap3 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1025 | w_NET_Sts_AlarmMap4 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1027 | w_NET_Sts_WarningAlarm | 1 | Byte-packed word | See Modbus_Status sheet for details (byte-packed). | N/A
| YES | Input Register | 1028 | w_NET_Sts_WarningMap1 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1030 | w_NET_Sts_WarningMap2 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1032 | w_NET_Sts_WarningMap3 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1034 | w_NET_Sts_WarningMap4 | 2 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1036 | w_NET_IN_Value1 | 1 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1037 | w_NET_OUT_Value1 | 1 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1038 | w_NET_IN_Error1 | 1 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1039 | w_NET_OUT_Error1 | 1 | Bit-packed word | See Modbus_Status sheet for details (bit-packed). | N/A
| YES | Input Register | 1040 | w_NET_Signal_Error1 | 2 | Nibble-packed word | See Modbus_Status sheet for details (nibble-packed). | N/A
| YES | Input Register | 1042 | w_NET_Signal_Error2 | 2 | Nibble-packed word | See Modbus_Status sheet for details (nibble-packed). | N/A
| YES | Input Register | 1044 | r_IN_SupplyRTD_Smoothed | 2 | Floating point | Temperature of the Supply (To Process) RTD, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C
| YES | Input Register | 1046 | r_IN_ReturnRTD_Smoothed | 2 | Floating point | Tempertaure of the Return (From Process) RTD, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C
| YES | Input Register | 1048 | r_SupplyReturnRTD_AvgSmoothed | 2 | Floating point | Average of the tempertaure of the Supply/Return (To/From Process) RTDs, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C
| YES | Input Register | 1050 | r_IN_RemoteRTD_Smoothed | 2 | Floating point | Tempertaure of the Remote RTD, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C
| YES | Input Register | 1052 | r_IN_AnalogProcessSmoothed | 2 | Floating point | Tempertaure of an extrernal process temperature signal, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. Not yet implemented. | °C
| YES | Input Register | 1054 | r_NET_ProcValueTempSmoothed | 2 | Floating point | Tempertaure of a network-provided process temperature signal, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. Not yet implemented. | °C
| YES | Input Register | 1056 | r_IN_SupplyPressureSmoothed | 2 | Floating point | Pressure measured by the Supply (To Process) transducer, smoothed with the display running average. Smootthing only occurs when unit is running. In units of psi. | psi
| YES | Input Register | 1058 | r_IN_ReturnPressureSmoothed | 2 | Floating point | Pressure measured by the Return (From Process) transducer, smoothed with the display running average. Smootthing only occurs when unit is running. In units of psi. | psi
| YES | Input Register | 1060 | r_EffectiveProcessValue | 2 | Floating point | The raw process value which is being utilized internally by the control loop. Not smoothed. In units of °C. | °C
| YES | Input Register | 1062 | r_FilteredEffectiveProcessValue | 2 | Floating point | The actual process value which is being utilized internally by the control loop, with filtering and smoothing applied. Smoothing only occurs when the unit is running. In units of °C. | °C
| YES | Input Register | 1064 | r_EffectiveSetpointValue | 2 | Floating point | The actual setpoint that is being utilized internally by the control loop. In units of °C. | °C
| YES | Input Register | 1066 | r_EstimatedFlowrate | 2 | Floating point | The estimated flowrate in the system. In units of gpm. | gpm
| YES | Input Register | 1068 | r_IN_SupplyRTD.Value | 2 | Floating point | Temperature of the Supply (To Process) RTD. No smoothing is applied. In units of °C. | °C
| YES | Input Register | 1070 | r_IN_ReturnRTD.Value | 2 | Floating point | Tempertaure of the Return (From Process) RTD. No smoothing is applied. In units of °C. | °C
| YES | Input Register | 1072 | r_SupplyReturnRTD_Avg | 2 | Floating point | Average of the tempertaure of the Supply/Return (To/From Process) RTDs. No smoothing is applied. In units of °C. | °C
| YES | Input Register | 1074 | r_IN_RemoteRTD.Value | 2 | Floating point | Tempertaure of the Remote RTD. In units of °C. No smoothing is applied. | °C
| YES | Input Register | 1076 | r_IN_AnalogProcess.Value | 2 | Floating point | Tempertaure of an extrernal process temperature signal. In units of °C. Not yet implemented. | °C
| YES | Input Register | 1078 | r_IN_AnalogSetpoint.Value | 2 | Floating point | Setpoint determined by an external analog signal. In units of °C. Not yet implemented. | °C
| YES | Input Register | 1080 | r_IN_SupplyPressure.Value | 2 | Floating point | Pressure measured by the Supply (To Process) transducer. No smoothing is applied. In units of psi. | psi
| YES | Input Register | 1082 | r_IN_ReturnPressure.Value | 2 | Floating point | Pressure measured by the Return (From Process) transducer. No smoothing is applied. In units of psi. | psi
| YES | Input Register | 1084 | r_IN_AnalogFlowmeter.Value | 2 | Floating point | Flow measured by an analog flow meter. In units of gpm. | gpm
| YES | Input Register | 1086 | r_IN_PulseFlowmeter.Value | 2 | Floating point | Flow measured by a pulse flow meter. Smoothing is applied. In units of gpm. | gpm
| YES | Input Register | 1088 | n_RampSoakActiveStep | 1 | Integer | The active step in the ramp/soak profile. | N/A
| YES | Input Register | 1089 | r_Flowmeter_Flowrate | 2 | Floating point | The flowrate measured by the flowmeter (pulse, analog or limit switch). If limit switch, it will be shown as 0.0 (low/bad flow) or 1.0 (flow). Otherwise, in units of gpm. | gpm
| YES | Input Register | 1091 | n_LowPressureStrikeCount | 2 | Integer | The number of low pressure pause events which could contribute to an eventual shutdown if more continue to occur. | events
| YES | Input Register | 1093 | r_NET_CoolingWaterTemperature | 2 | Floating point | The temperature of the cooling water, as measured at the end of the valve vent. In units of °C. | °C
| YES | Input Register | 1095 | r_HotPressureNextReleaseTemp | 2 | Floating point | The temperature at which the next hot pressure release will occur. Only valid when using temperature-based pressure relief, otherwise 0 when using pressure-based pressure relief. In units of °C. | °C
| YES | Input Register | 1097 | n_PID_SteadyStateTime | 2 | Integer | How long the unit has detected a continuous steady-state condition. In units of seconds. | seconds
| YES | Input Register | 1099 | r_ActiveHeatToCoolOutRatio | 2 | Floating point | The current ratio of heating strength vs cooling strength on the PID loop output. | N/A
| YES | Discrete Input | 1036 | b_EstimatedFlowrateValid | 1 | Bool | Internally computed values. | Yes/No
| YES | Discrete Input | 1037 | b_WarningActive | 1 | Bool | High if any warnings active. | Yes/No
| YES | Discrete Input | 1038 | b_AlarmActive | 1 | Bool | High if any alarms active. | Yes/No
| YES | Discrete Input | 1039 | b_EnableRampSoak | 1 | Bool | Enumerated value: FALSE=Ramp/Soak Disabled; TRUE=Ramp/Soak Enabled; | Yes/No
| YES | Discrete Input | 1040 | b_PAR_TempUnits.CurrentValue | 1 | Bool | Enumerated value: FALSE=Fahrenheit; TRUE=Celsius. | <enumeration>
| YES | Discrete Input | 1041 | b_PAR_FlowUnits.CurrentValue | 1 | Bool | Enumerated value: FALSE=Gallons; TRUE=Liters. | <enumeration>
| YES | Discrete Input | 1042 | b_PAR_PressureUnits.CurrentValue | 1 | Bool | Enumerated value: FALSE=psi; TRUE=bar. | <enumeration>
Parameters, intended for individual read and writing only as necessary.
| YES | Input Register | 2000 | n_PAR_TCU_Type.CurrentValue | 2 | Integer | Brand and model of this unit. Enumerated value: IF b_PAR_OEM_Product.CurrentValue=FALSE: 0="Unbranded"; 1="Conair TW-B"; 2="Conair TW-E"; 3="Conair TW-T"; 4="TC RQT Std"; 5="TC RQT Adv"; 6="TC RQT Prem"; IF b_PAR_OEM_Product.CurrentValue=TRUE: 0="Unbranded"; 1="Type C Low"; 2="Type C Mid"; 3="Type C HIgh"; 4="Type T Low"; 5="Type T Mid"; 6="Type T High". | <enumeration>
| YES | Discrete Input | 2000 | n_PAR_TCU_Type.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2002 | n_PAR_TCU_Type.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2004 | n_PAR_TCU_Type.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2001 | n_PAR_TCU_Type.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2000 | n_PAR_TCU_Type.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Discrete Input | 2010 | b_PAR_MoldPurgeInstalled.CurrentValue | 1 | Bool | Tells the controller if mold purge plumbing is installed. Enumerated value: FALSE="Mold Purge" option not installed; TRUE="Mold Purge" option installed. | <enumeration>
| YES | Discrete Input | 2011 | b_PAR_MoldPurgeInstalled.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2012 | b_PAR_MoldPurgeInstalled.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2010 | b_PAR_MoldPurgeInstalled.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 2020 | b_PAR_PhaseMonitorInstalled.CurrentValue | 1 | Bool | Tells the controller if phase detection hardware is installed. Enumerated value: FALSE="Phase Monitor" not installed; TRUE="Phase Monitor" is installed. | <enumeration>
| YES | Discrete Input | 2021 | b_PAR_PhaseMonitorInstalled.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2022 | b_PAR_PhaseMonitorInstalled.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2020 | b_PAR_PhaseMonitorInstalled.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 2030 | n_PAR_HeaterControlType.CurrentValue | 2 | Integer | Type of heater switching device and whether or not monitoring contacts provide feedback to the controller regarding contactor state. Enumerated value: 0="No Heat"; 1="E-Mech Contactor"; 2="SSR"; 3="Mercury". | <enumeration>
| YES | Discrete Input | 2030 | n_PAR_HeaterControlType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2032 | n_PAR_HeaterControlType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2034 | n_PAR_HeaterControlType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2031 | n_PAR_HeaterControlType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2030 | n_PAR_HeaterControlType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2040 | n_PAR_PumpVoltageFreq.CurrentValue | 2 | Integer | Selects the installed pump voltage and frequency. Enumerated value: 0="Not Selected"; 1="460 V / 60 Hz"; 2="208 V / 60 Hz"; 3="230 V / 60 Hz"; 4="380 V / 60Hz"; 5="400 V / 50 Hz"; 6="575 V / 60 Hz". | <enumeration>
| YES | Discrete Input | 2040 | n_PAR_PumpVoltageFreq.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2042 | n_PAR_PumpVoltageFreq.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2044 | n_PAR_PumpVoltageFreq.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2041 | n_PAR_PumpVoltageFreq.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2040 | n_PAR_PumpVoltageFreq.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2050 | n_PAR_PumpHP.CurrentValue | 2 | Integer | Selects the nominal horsepower of the pump. Enumerated value: 0="Not Selected"; 1="0.5 HP"; 2="0.75 HP"; 3="1 HP"; 4="2 HP"; 5="3 HP"; 6="5 HP"; 7="7.5 HP"; 8="10 HP". | <enumeration>
| YES | Discrete Input | 2050 | n_PAR_PumpHP.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2052 | n_PAR_PumpHP.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2054 | n_PAR_PumpHP.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2051 | n_PAR_PumpHP.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2050 | n_PAR_PumpHP.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2060 | n_PAR_HeaterKW.CurrentValue | 2 | Integer | Selects the installed heater size. Enumerated value: 0="None"; 1="9 kW"; 2="12 kW"; 3="18 kW"; 4="24 kW"; 5="36 kW"; or 6="48 kW". | <enumeration>
| YES | Discrete Input | 2060 | n_PAR_HeaterKW.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2062 | n_PAR_HeaterKW.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2064 | n_PAR_HeaterKW.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2061 | n_PAR_HeaterKW.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2060 | n_PAR_HeaterKW.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2070 | n_PAR_ReturnHardware.CurrentValue | 2 | Integer | Selects the installed hardware on the "From Process" side of the pump. Enumerated value: 0="Mixing Tank"; 1="Std Perf Heat Ex"; 2="High Perf Heat Ex"; 3="Heater". | <enumeration>
| YES | Discrete Input | 2070 | n_PAR_ReturnHardware.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2072 | n_PAR_ReturnHardware.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2074 | n_PAR_ReturnHardware.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2071 | n_PAR_ReturnHardware.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2070 | n_PAR_ReturnHardware.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2080 | n_PAR_MaxTempConfig.CurrentValue | 2 | Integer | Selects the hardware configuration for maximum process loop temperature Enumerated value: 0="250°F"; 1="300°F". | <enumeration>
| YES | Discrete Input | 2080 | n_PAR_MaxTempConfig.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2082 | n_PAR_MaxTempConfig.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2084 | n_PAR_MaxTempConfig.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2081 | n_PAR_MaxTempConfig.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2080 | n_PAR_MaxTempConfig.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2090 | n_PAR_CoolingValveType.CurrentValue | 2 | Integer | Selects what kind of cooling valve is connected to the unit. Enumerated value: 0="None"; 1="Solenoid"; 2="Modulating"; 3="Floating" (not yet implemented). | <enumeration>
| YES | Discrete Input | 2090 | n_PAR_CoolingValveType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2092 | n_PAR_CoolingValveType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2094 | n_PAR_CoolingValveType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2091 | n_PAR_CoolingValveType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2090 | n_PAR_CoolingValveType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2100 | n_PAR_ModCoolingValveCv.CurrentValue | 2 | Integer | Specifies the Cv of the modulating cooling valve. (Cv=Number of gallons through the valve per minute at a 1psi pressure drop.) Enumerated value: 0="Not Selected", 1="1.2 Cv", 2="2.9 Cv", 3="4.7 Cv", 4= "7.4 Cv", 5="11.7 Cv", 6="24 Cv", 7="30 Cv". | <enumeration>
| YES | Discrete Input | 2100 | n_PAR_ModCoolingValveCv.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2102 | n_PAR_ModCoolingValveCv.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2104 | n_PAR_ModCoolingValveCv.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2101 | n_PAR_ModCoolingValveCv.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2100 | n_PAR_ModCoolingValveCv.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| NO | Input Register | 2110 | n_PAR_SolCoolingValveCv.CurrentValue | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 2110 | n_PAR_SolCoolingValveCv.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2112 | n_PAR_SolCoolingValveCv.Maximum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 2114 | n_PAR_SolCoolingValveCv.Minimum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 2111 | n_PAR_SolCoolingValveCv.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2110 | n_PAR_SolCoolingValveCv.RemoteValue | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Input Register | 2120 | n_PAR_CV_PressReliefDuration.CurrentValue | 2 | Integer | How long to keep cooling valve open when performing an automatic hot pressure relief. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 2120 | n_PAR_CV_PressReliefDuration.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2122 | n_PAR_CV_PressReliefDuration.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 2124 | n_PAR_CV_PressReliefDuration.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 2121 | n_PAR_CV_PressReliefDuration.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2120 | n_PAR_CV_PressReliefDuration.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 2130 | n_PAR_CV_FullStrokeDuration.CurrentValue | 2 | Integer | Time for cooling valve to traverse from fully closed to fully open. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 2130 | n_PAR_CV_FullStrokeDuration.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2132 | n_PAR_CV_FullStrokeDuration.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 2134 | n_PAR_CV_FullStrokeDuration.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 2131 | n_PAR_CV_FullStrokeDuration.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2130 | n_PAR_CV_FullStrokeDuration.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 2140 | r_PAR_CV_ValveMinPosition.CurrentValue | 2 | Floating point | Maximum cooling valve actuator position where the valve will have no flow. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 2140 | r_PAR_CV_ValveMinPosition.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2142 | r_PAR_CV_ValveMinPosition.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 2144 | r_PAR_CV_ValveMinPosition.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 2141 | r_PAR_CV_ValveMinPosition.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2140 | r_PAR_CV_ValveMinPosition.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 2150 | r_PAR_CV_ValveMaxPosition.CurrentValue | 2 | Floating point | Minimum cooling valve actuator position where the valve will have full flow. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 2150 | r_PAR_CV_ValveMaxPosition.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2152 | r_PAR_CV_ValveMaxPosition.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 2154 | r_PAR_CV_ValveMaxPosition.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 2151 | r_PAR_CV_ValveMaxPosition.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2150 | r_PAR_CV_ValveMaxPosition.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 2160 | r_PAR_CV_UtilizedRange.CurrentValue | 2 | Floating point | Maximum cooling valve actuator position used to limit cooling. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 2160 | r_PAR_CV_UtilizedRange.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2162 | r_PAR_CV_UtilizedRange.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 2164 | r_PAR_CV_UtilizedRange.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 2161 | r_PAR_CV_UtilizedRange.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2160 | r_PAR_CV_UtilizedRange.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 2170 | r_PAR_CV_PressureReliefOpenAmt.CurrentValue | 2 | Floating point | How far to open the cooling valve when performing an automatic hot pressure relief. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 2170 | r_PAR_CV_PressureReliefOpenAmt.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2172 | r_PAR_CV_PressureReliefOpenAmt.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 2174 | r_PAR_CV_PressureReliefOpenAmt.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 2171 | r_PAR_CV_PressureReliefOpenAmt.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2170 | r_PAR_CV_PressureReliefOpenAmt.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 2180 | n_PAR_AnalogProcRetransmitType.CurrentValue | 2 | Integer | Analog input type for process temperature retransmit. Enumerated value: 0="None"; 1="4-20mA"; 2="0-10V". | <enumeration>
| YES | Discrete Input | 2180 | n_PAR_AnalogProcRetransmitType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2182 | n_PAR_AnalogProcRetransmitType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2184 | n_PAR_AnalogProcRetransmitType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2181 | n_PAR_AnalogProcRetransmitType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2180 | n_PAR_AnalogProcRetransmitType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| NO | Input Register | 2190 | n_PAR_AnalogSetpointType.CurrentValue | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 2190 | n_PAR_AnalogSetpointType.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2192 | n_PAR_AnalogSetpointType.Maximum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 2194 | n_PAR_AnalogSetpointType.Minimum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 2191 | n_PAR_AnalogSetpointType.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2190 | n_PAR_AnalogSetpointType.RemoteValue | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 2200 | n_PAR_AnalogProcessInputType.CurrentValue | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 2200 | n_PAR_AnalogProcessInputType.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2202 | n_PAR_AnalogProcessInputType.Maximum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 2204 | n_PAR_AnalogProcessInputType.Minimum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 2201 | n_PAR_AnalogProcessInputType.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2200 | n_PAR_AnalogProcessInputType.RemoteValue | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Input Register | 2210 | n_PAR_AutoLogoutTimeout.CurrentValue | 2 | Integer | Duration of touchscreen inactivity before logged-in user reverts back to the default security level. This is the current value for this parameter used in operation of the unit. | minutes
| YES | Discrete Input | 2210 | n_PAR_AutoLogoutTimeout.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2212 | n_PAR_AutoLogoutTimeout.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Input Register | 2214 | n_PAR_AutoLogoutTimeout.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Discrete Input | 2211 | n_PAR_AutoLogoutTimeout.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2210 | n_PAR_AutoLogoutTimeout.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes
| YES | Input Register | 2220 | n_PAR_FlowmeterType.CurrentValue | 2 | Integer | The type of flowmeter attached to the unit. Enumerated value: 0="None"; 1="Pulse Rate"; 2="Limit Switch"; 3="Analog 4-20mA"; 4="Analog 0-10V". | <enumeration>
| YES | Discrete Input | 2220 | n_PAR_FlowmeterType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2222 | n_PAR_FlowmeterType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2224 | n_PAR_FlowmeterType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2221 | n_PAR_FlowmeterType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2220 | n_PAR_FlowmeterType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2230 | n_PAR_ReturnTransducerType.CurrentValue | 2 | Integer | Selects the From Process pressure transducer (or pressure switch) type. Enumerated value: 0="Switch"; 1="Installed"; 2="Bypass". | <enumeration>
| YES | Discrete Input | 2230 | n_PAR_ReturnTransducerType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2232 | n_PAR_ReturnTransducerType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2234 | n_PAR_ReturnTransducerType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2231 | n_PAR_ReturnTransducerType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2230 | n_PAR_ReturnTransducerType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2240 | n_PAR_SupplyTransducerType.CurrentValue | 2 | Integer | Selects the To Process pressure transducer type. Enumerated value: 0="None"; 1="Installed". | <enumeration>
| YES | Discrete Input | 2240 | n_PAR_SupplyTransducerType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2242 | n_PAR_SupplyTransducerType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2244 | n_PAR_SupplyTransducerType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2241 | n_PAR_SupplyTransducerType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2240 | n_PAR_SupplyTransducerType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2250 | n_PAR_Altitude.CurrentValue | 2 | Integer | Altitude at which the machine is installed, in order to properly calculate atmospheric pressure. This is the current value for this parameter used in operation of the unit. In units of ft. | ft
| YES | Discrete Input | 2250 | n_PAR_Altitude.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2252 | n_PAR_Altitude.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | ft
| YES | Input Register | 2254 | n_PAR_Altitude.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | ft
| YES | Discrete Input | 2251 | n_PAR_Altitude.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2250 | n_PAR_Altitude.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | ft
| YES | Input Register | 2260 | r_PAR_AMSP_BoilingMargin.CurrentValue | 2 | Floating point | How many degrees of margin are added to the boiling point calculation. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 2260 | r_PAR_AMSP_BoilingMargin.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2262 | r_PAR_AMSP_BoilingMargin.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 2264 | r_PAR_AMSP_BoilingMargin.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 2261 | r_PAR_AMSP_BoilingMargin.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2260 | r_PAR_AMSP_BoilingMargin.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Discrete Input | 2270 | b_PAR_AlarmOutputReverseActing.CurrentValue | 1 | Bool | Flips the output behavior of the non-slienceable alarm output. Enumerated value: FALSE=Non-sileanceable alarm output is active when alarm is active; TRUE=Non-sileanceable alarm output is active when alarm is NOT active. | <enumeration>
| YES | Discrete Input | 2271 | b_PAR_AlarmOutputReverseActing.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2272 | b_PAR_AlarmOutputReverseActing.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2270 | b_PAR_AlarmOutputReverseActing.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 2280 | r_PAR_MaxTempSetpoint.CurrentValue | 2 | Floating point | Maximum permitted setpoint for this machine, when operating at sufficient pressure. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2280 | r_PAR_MaxTempSetpoint.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2282 | r_PAR_MaxTempSetpoint.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2284 | r_PAR_MaxTempSetpoint.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2281 | r_PAR_MaxTempSetpoint.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2280 | r_PAR_MaxTempSetpoint.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2290 | r_PAR_MinTempSetpoint.CurrentValue | 2 | Floating point | Minimum permitted setpoint for this machine. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2290 | r_PAR_MinTempSetpoint.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2292 | r_PAR_MinTempSetpoint.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2294 | r_PAR_MinTempSetpoint.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2291 | r_PAR_MinTempSetpoint.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2290 | r_PAR_MinTempSetpoint.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2300 | r_PAR_MaxHeaterDutyCycle.CurrentValue | 2 | Floating point | Maximum PWM duty cycle for the heater. Can be used to limit heating or electrical amps. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 2300 | r_PAR_MaxHeaterDutyCycle.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2302 | r_PAR_MaxHeaterDutyCycle.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 2304 | r_PAR_MaxHeaterDutyCycle.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 2301 | r_PAR_MaxHeaterDutyCycle.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2300 | r_PAR_MaxHeaterDutyCycle.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 2310 | n_PAR_SerialNumber.CurrentValue | 2 | Integer | Serial number of the machine. This is the current value for this parameter used in operation of the unit. | N/A
| YES | Discrete Input | 2310 | n_PAR_SerialNumber.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2312 | n_PAR_SerialNumber.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | N/A
| YES | Input Register | 2314 | n_PAR_SerialNumber.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | N/A
| YES | Discrete Input | 2311 | n_PAR_SerialNumber.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2310 | n_PAR_SerialNumber.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | N/A
| YES | Input Register | 2320 | r_PAR_FactoryTempHighAlarm.CurrentValue | 2 | Floating point | Process temperature at which a high temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2320 | r_PAR_FactoryTempHighAlarm.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2322 | r_PAR_FactoryTempHighAlarm.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2324 | r_PAR_FactoryTempHighAlarm.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2321 | r_PAR_FactoryTempHighAlarm.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2320 | r_PAR_FactoryTempHighAlarm.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2330 | r_PAR_FactoryTempLowAlarm.CurrentValue | 2 | Floating point | Process temperature at which a low temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2330 | r_PAR_FactoryTempLowAlarm.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2332 | r_PAR_FactoryTempLowAlarm.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2334 | r_PAR_FactoryTempLowAlarm.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2331 | r_PAR_FactoryTempLowAlarm.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2330 | r_PAR_FactoryTempLowAlarm.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2340 | r_PAR_MinPressToRun.CurrentValue | 2 | Floating point | Minimum pressure required to operate at low temperatures. This is the current value for this parameter used in operation of the unit. In units of psi. | psi
| YES | Discrete Input | 2340 | r_PAR_MinPressToRun.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2342 | r_PAR_MinPressToRun.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | psi
| YES | Input Register | 2344 | r_PAR_MinPressToRun.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | psi
| YES | Discrete Input | 2341 | r_PAR_MinPressToRun.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2340 | r_PAR_MinPressToRun.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | psi
| YES | Discrete Input | 2350 | b_PAR_RemoteStartEnable.CurrentValue | 1 | Bool | Allows the unit to be started with an externally-switched digital input. Enumerated value: FALSE=Do not allow "Remote Start"; TRUE=Allow "Remote Start". | <enumeration>
| YES | Discrete Input | 2351 | b_PAR_RemoteStartEnable.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2352 | b_PAR_RemoteStartEnable.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2350 | b_PAR_RemoteStartEnable.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 2360 | b_PAR_AutoRestartEnable.CurrentValue | 1 | Bool | Causes the unit to automatically restart if power was lost while the unit was running. Enumerated value: FALSE=Do not allow "Auto Restart"; TRUE=Allow "Auto Restart". | <enumeration>
| YES | Discrete Input | 2361 | b_PAR_AutoRestartEnable.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2362 | b_PAR_AutoRestartEnable.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2360 | b_PAR_AutoRestartEnable.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 2370 | n_PAR_AutoRestartDelay.CurrentValue | 2 | Integer | How long to wait before auto-restarting the machine once electrical power is restored. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2370 | n_PAR_AutoRestartDelay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2372 | n_PAR_AutoRestartDelay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2374 | n_PAR_AutoRestartDelay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2371 | n_PAR_AutoRestartDelay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2370 | n_PAR_AutoRestartDelay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Discrete Input | 2380 | b_PAR_BrownoutMonitorEnable.CurrentValue | 1 | Bool | Causes the unit to alarm upon return of power if the unit was running when power was lost. Enumerated value: FALSE=Do not enable "Brownout Monitor"; TRUE=Enable "Brownout Monitor". | <enumeration>
| YES | Discrete Input | 2381 | b_PAR_BrownoutMonitorEnable.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2382 | b_PAR_BrownoutMonitorEnable.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2380 | b_PAR_BrownoutMonitorEnable.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 2390 | b_PAR_TempUnits.CurrentValue | 1 | Bool | Selects whether temperature units are displayed in Fahrenheit or Celsius. Enumerated value: FALSE=Fahrenheit; TRUE=Celsius. | <enumeration>
| YES | Discrete Input | 2391 | b_PAR_TempUnits.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2392 | b_PAR_TempUnits.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2390 | b_PAR_TempUnits.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 2400 | b_PAR_FlowUnits.CurrentValue | 1 | Bool | Selects whether flow units are displayed in gallons or liters. Enumerated value: FALSE=Gallons; TRUE=Liters. | <enumeration>
| YES | Discrete Input | 2401 | b_PAR_FlowUnits.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2402 | b_PAR_FlowUnits.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2400 | b_PAR_FlowUnits.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 2410 | b_PAR_PressureUnits.CurrentValue | 1 | Bool | Selects whether pressure is displayed in psi or bar. Enumerated value: FALSE=psi; TRUE=bar. | <enumeration>
| YES | Discrete Input | 2411 | b_PAR_PressureUnits.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2412 | b_PAR_PressureUnits.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2410 | b_PAR_PressureUnits.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 2420 | n_PAR_GlobalUnits.CurrentValue | 2 | Integer | Selects Imperial US or Metric units of measure for all numbers displayed on the touchscreen. Enumerated value: 0="Custom", 1="Imperial US", 2="Metric". | <enumeration>
| YES | Discrete Input | 2420 | n_PAR_GlobalUnits.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2422 | n_PAR_GlobalUnits.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2424 | n_PAR_GlobalUnits.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2421 | n_PAR_GlobalUnits.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2420 | n_PAR_GlobalUnits.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2430 | n_PAR_BootupSecurityLevel.CurrentValue | 2 | Integer | The user level that will be defaultly logged in at bootup, or when an elevated user logs out. Enumerated value: 0="Guest"; 1="Operator"; 2="Setup"; 3="Service"; 4="Administrator". | <enumeration>
| YES | Discrete Input | 2430 | n_PAR_BootupSecurityLevel.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2432 | n_PAR_BootupSecurityLevel.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2434 | n_PAR_BootupSecurityLevel.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2431 | n_PAR_BootupSecurityLevel.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2430 | n_PAR_BootupSecurityLevel.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2440 | n_PAR_BacklightTimeout.CurrentValue | 2 | Integer | Duration of touchscreen inactivity before the screen backlight is dimmed. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2440 | n_PAR_BacklightTimeout.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2442 | n_PAR_BacklightTimeout.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2444 | n_PAR_BacklightTimeout.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2441 | n_PAR_BacklightTimeout.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2440 | n_PAR_BacklightTimeout.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2450 | n_PAR_ScreenSaverTimeout.CurrentValue | 2 | Integer | Duration of touchscreen inactivity before the screensaver is activated. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2450 | n_PAR_ScreenSaverTimeout.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2452 | n_PAR_ScreenSaverTimeout.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2454 | n_PAR_ScreenSaverTimeout.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2451 | n_PAR_ScreenSaverTimeout.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2450 | n_PAR_ScreenSaverTimeout.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2460 | n_PAR_HomeScreenKPI_Left.CurrentValue | 2 | Integer | Defines which KPI will be shown on the left space of the home screen. Enumerated value: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate". | <enumeration>
| YES | Discrete Input | 2460 | n_PAR_HomeScreenKPI_Left.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2462 | n_PAR_HomeScreenKPI_Left.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2464 | n_PAR_HomeScreenKPI_Left.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2461 | n_PAR_HomeScreenKPI_Left.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2460 | n_PAR_HomeScreenKPI_Left.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2470 | n_PAR_HomeScreenKPI_Right.CurrentValue | 2 | Integer | Defines which KPI will be shown on the right space of the home screen. Enumerated value: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate". | <enumeration>
| YES | Discrete Input | 2470 | n_PAR_HomeScreenKPI_Right.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2472 | n_PAR_HomeScreenKPI_Right.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2474 | n_PAR_HomeScreenKPI_Right.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2471 | n_PAR_HomeScreenKPI_Right.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2470 | n_PAR_HomeScreenKPI_Right.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2480 | n_PAR_HomeScreenKPI_Screensaver.CurrentValue | 2 | Integer | Defines which KPI will be shown on the screensaver. Enumerated value: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate". | <enumeration>
| YES | Discrete Input | 2480 | n_PAR_HomeScreenKPI_Screensaver.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2482 | n_PAR_HomeScreenKPI_Screensaver.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2484 | n_PAR_HomeScreenKPI_Screensaver.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2481 | n_PAR_HomeScreenKPI_Screensaver.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2480 | n_PAR_HomeScreenKPI_Screensaver.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| NO | Discrete Input | 2490 | b_PAR_DisplayFilteredPV.CurrentValue | 1 | Bool | Defines which KPI will be shown on the screensaver. Enumerated value: FALSE=Display raw process value with no smoothing and no dynamic deadband.; TRUE=Display smoothed and dynamic deadbanded process value. | <enumeration>
| NO | Discrete Input | 2491 | b_PAR_DisplayFilteredPV.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| NO | Discrete Input | 2492 | b_PAR_DisplayFilteredPV.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| NO | Coil | 2490 | b_PAR_DisplayFilteredPV.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 2500 | n_PAR_HotPressReliefThreshold.CurrentValue | 2 | Integer | How many degrees in temperature rise should the unit wait before relieving process pressure as a result of thermal expansion. Enumerated value: 0="Disabled"; 1="Auto"; 2="5°F"/"2.78°C"; 3="10°F"/"5.56°C"; 4="15°F"/"8.33°C"; 5="20°F"/"11.1°C"; 6="25°F"/"13.8°C"; 7="30°F"/"16.6°C"; 8="40°F"/"22.2°C"; 9="50°F"/"27.7°C"; 10="70°F"/"38.8°C"; 11="90°F"/"50.0°C"; 12="110°F"/"61.1°C"; 13="130°F"/"72.2°C"; 14="150°F"/"83.3°C"; 15="170°F"/"94.4°C"; 16="200°F"/"111.1°C". | <enumeration>
| YES | Discrete Input | 2500 | n_PAR_HotPressReliefThreshold.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2502 | n_PAR_HotPressReliefThreshold.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2504 | n_PAR_HotPressReliefThreshold.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2501 | n_PAR_HotPressReliefThreshold.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2500 | n_PAR_HotPressReliefThreshold.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2510 | n_PAR_VentDurationStage1.CurrentValue | 2 | Integer | Duration of the vent cycle with only the cooling valve open (no pump). This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2510 | n_PAR_VentDurationStage1.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2512 | n_PAR_VentDurationStage1.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2514 | n_PAR_VentDurationStage1.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2511 | n_PAR_VentDurationStage1.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2510 | n_PAR_VentDurationStage1.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2520 | n_PAR_VentDurationStage2.CurrentValue | 2 | Integer | Duration of the vent cycle with both the cooling valve open and the pump running. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2520 | n_PAR_VentDurationStage2.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2522 | n_PAR_VentDurationStage2.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2524 | n_PAR_VentDurationStage2.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2521 | n_PAR_VentDurationStage2.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2520 | n_PAR_VentDurationStage2.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2530 | r_PAR_VentBypassTemp.CurrentValue | 2 | Floating point | Process temperature above which the vent cycles will be skipped. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2530 | r_PAR_VentBypassTemp.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2532 | r_PAR_VentBypassTemp.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2534 | r_PAR_VentBypassTemp.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2531 | r_PAR_VentBypassTemp.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2530 | r_PAR_VentBypassTemp.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2540 | n_PAR_LowPressRecoveryDelay.CurrentValue | 2 | Integer | Wait time before automatically restarting a paused machine once pressure is restored. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 2540 | n_PAR_LowPressRecoveryDelay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2542 | n_PAR_LowPressRecoveryDelay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 2544 | n_PAR_LowPressRecoveryDelay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 2541 | n_PAR_LowPressRecoveryDelay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2540 | n_PAR_LowPressRecoveryDelay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 2550 | n_PAR_LowPressRideThrough.CurrentValue | 2 | Integer | How long to ignore a low pressure condition before pausing machine operation. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 2550 | n_PAR_LowPressRideThrough.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2552 | n_PAR_LowPressRideThrough.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 2554 | n_PAR_LowPressRideThrough.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 2551 | n_PAR_LowPressRideThrough.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2550 | n_PAR_LowPressRideThrough.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 2560 | n_PAR_LowPressStandbyTO.CurrentValue | 2 | Integer | Exceeding this timeout, while paused due to low pressure, will abandon efforts for an auto-restart. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes
| YES | Discrete Input | 2560 | n_PAR_LowPressStandbyTO.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2562 | n_PAR_LowPressStandbyTO.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Input Register | 2564 | n_PAR_LowPressStandbyTO.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Discrete Input | 2561 | n_PAR_LowPressStandbyTO.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2560 | n_PAR_LowPressStandbyTO.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes
| YES | Input Register | 2570 | n_PAR_LowPressStrikesPermitted.CurrentValue | 2 | Integer | Maximum low pressure events permitted which will still result in auto-restart if pressure is restored. This is the current value for this parameter used in operation of the unit. In units of events. | events
| YES | Discrete Input | 2570 | n_PAR_LowPressStrikesPermitted.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2572 | n_PAR_LowPressStrikesPermitted.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | events
| YES | Input Register | 2574 | n_PAR_LowPressStrikesPermitted.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | events
| YES | Discrete Input | 2571 | n_PAR_LowPressStrikesPermitted.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2570 | n_PAR_LowPressStrikesPermitted.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | events
| YES | Input Register | 2580 | n_PAR_LowPressStrikesTimer.CurrentValue | 2 | Integer | Rolling time period over which low pressure events are counted to permit/deny an auto-restart. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes
| YES | Discrete Input | 2580 | n_PAR_LowPressStrikesTimer.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2582 | n_PAR_LowPressStrikesTimer.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Input Register | 2584 | n_PAR_LowPressStrikesTimer.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Discrete Input | 2581 | n_PAR_LowPressStrikesTimer.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2580 | n_PAR_LowPressStrikesTimer.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes
| YES | Input Register | 2590 | n_PAR_AdaptiveMaxSetpoint.CurrentValue | 2 | Integer | Active enumerated value: 0="Variable"; 1="Fixed 180°F"; 2="Fixed 190°F"; 3="Fixed 200°F"; 4="Fixed 210°F"; 5="Fixed 220°F"; 6="Fixed 230°F"; 7="Fixed 240°F"; 8="Fixed 250°F"; 9="Fixed 260°F"; 10="Fixed 270°F"; 11="Fixed 280°F"; 12="Fixed 290°F"; 13="Fixed 300°F". | <enumeration>
| YES | Discrete Input | 2590 | n_PAR_AdaptiveMaxSetpoint.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2592 | n_PAR_AdaptiveMaxSetpoint.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2594 | n_PAR_AdaptiveMaxSetpoint.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2591 | n_PAR_AdaptiveMaxSetpoint.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2590 | n_PAR_AdaptiveMaxSetpoint.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2600 | n_PAR_RunLowPressAction.CurrentValue | 2 | Integer | Selects the reaction to a low pressure condition when the unit is RUNNING. Enumerated value: 0="Pause"; 1="Wrn & Lower SP"; 2="Wrn & Lower SP (Tracking)"; 3="Only Alarm (Stop)"; 4="Alarm (Stop) & Lower SP"; 5="Max SP Tracking". | <enumeration>
| YES | Discrete Input | 2600 | n_PAR_RunLowPressAction.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2602 | n_PAR_RunLowPressAction.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2604 | n_PAR_RunLowPressAction.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2601 | n_PAR_RunLowPressAction.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2600 | n_PAR_RunLowPressAction.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2610 | n_PAR_StopLowPressAction.CurrentValue | 2 | Integer | Selects the reaction to a low pressure condition when the unit is STOPPED. Enumerated value: 0="Warning"; 1="Warning & Lower SP"; 2="Warning & Lower (Tracking)"; 3="Alarm"; 4="Alarm & Lower SP"; 5="Max Tracking". | <enumeration>
| YES | Discrete Input | 2610 | n_PAR_StopLowPressAction.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2612 | n_PAR_StopLowPressAction.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2614 | n_PAR_StopLowPressAction.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2611 | n_PAR_StopLowPressAction.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2610 | n_PAR_StopLowPressAction.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2620 | n_PAR_AdaptiveMaxSP_PressAvg.CurrentValue | 2 | Integer | How much smoothing to apply to the measured process pressure. This is the current value for this parameter used in operation of the unit. | seconds
| YES | Discrete Input | 2620 | n_PAR_AdaptiveMaxSP_PressAvg.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2622 | n_PAR_AdaptiveMaxSP_PressAvg.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2624 | n_PAR_AdaptiveMaxSP_PressAvg.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2621 | n_PAR_AdaptiveMaxSP_PressAvg.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2620 | n_PAR_AdaptiveMaxSP_PressAvg.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2630 | n_PAR_BootupDuration.CurrentValue | 2 | Integer | Duration between powerup and first scan of the application program. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 2630 | n_PAR_BootupDuration.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2632 | n_PAR_BootupDuration.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 2634 | n_PAR_BootupDuration.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 2631 | n_PAR_BootupDuration.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2630 | n_PAR_BootupDuration.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 2640 | n_PAR_MoldPurgeTO.CurrentValue | 2 | Integer | Maximum duration of a mold purge cycle. Purging will be cancelled if this duration is exceeded. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2640 | n_PAR_MoldPurgeTO.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2642 | n_PAR_MoldPurgeTO.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2644 | n_PAR_MoldPurgeTO.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2641 | n_PAR_MoldPurgeTO.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2640 | n_PAR_MoldPurgeTO.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Discrete Input | 2650 | b_PAR_FlowswitchTrip.CurrentValue | 1 | Bool | Selects whether low flow is detected by a flowswitch low or high signal. Enumerated value: FALSE=Trip flow alarm on flowswitch contacts open; TRUE=Trip flow alarm on flowswitch contacts closed. | <enumeration>
| YES | Discrete Input | 2651 | b_PAR_FlowswitchTrip.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2652 | b_PAR_FlowswitchTrip.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2650 | b_PAR_FlowswitchTrip.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 2660 | b_PAR_NetworkHeatCoolEnable.CurrentValue | 1 | Bool | Turns on the ability for the unit to receive heat/cool requests from the network connection. Enumerated value: FALSE=Ignore heat/cool signals from the network.; TRUE=Allow heat/cool signals from the network to be acted upon. Not yet implemented. | <enumeration>
| YES | Discrete Input | 2661 | b_PAR_NetworkHeatCoolEnable.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 2662 | b_PAR_NetworkHeatCoolEnable.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 2660 | b_PAR_NetworkHeatCoolEnable.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 2670 | n_PAR_CooldownMaxTime.CurrentValue | 2 | Integer | If a full cooldown cannot be achieved within this timeframe, the machine will simply stop. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2670 | n_PAR_CooldownMaxTime.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2672 | n_PAR_CooldownMaxTime.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2674 | n_PAR_CooldownMaxTime.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2671 | n_PAR_CooldownMaxTime.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2670 | n_PAR_CooldownMaxTime.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2680 | n_PAR_CooldownMinTime.CurrentValue | 2 | Integer | If a full cooldown is achieved before this timeframe, the machine will continue to cool until this time. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2680 | n_PAR_CooldownMinTime.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2682 | n_PAR_CooldownMinTime.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2684 | n_PAR_CooldownMinTime.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2681 | n_PAR_CooldownMinTime.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2680 | n_PAR_CooldownMinTime.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2690 | n_PAR_DeviationAction.CurrentValue | 2 | Integer | Specifies the action that should be taken when a temperature deviation is detected. Enumerated value: 0="Do Nothing"; 1="Warning"; 2="Alarm". | <enumeration>
| YES | Discrete Input | 2690 | n_PAR_DeviationAction.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2692 | n_PAR_DeviationAction.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2694 | n_PAR_DeviationAction.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2691 | n_PAR_DeviationAction.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2690 | n_PAR_DeviationAction.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2700 | n_PAR_FlowmeterK_Factor.CurrentValue | 2 | Integer | K-factor of the pulse flowmeter, as determined by the flowmeter's last calibration. This is the current value for this parameter used in operation of the unit. In units of pulses/gal. | pulses/gal
| YES | Discrete Input | 2700 | n_PAR_FlowmeterK_Factor.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2702 | n_PAR_FlowmeterK_Factor.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | pulses/gal
| YES | Input Register | 2704 | n_PAR_FlowmeterK_Factor.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | pulses/gal
| YES | Discrete Input | 2701 | n_PAR_FlowmeterK_Factor.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2700 | n_PAR_FlowmeterK_Factor.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | pulses/gal
| YES | Input Register | 2710 | n_PAR_FlowmeterTripAction.CurrentValue | 2 | Integer | Specifies the action that should be taken when the flowswitch or flowmeter is tripped. Enumerated value: 0="Do Nothing"; 1="Warning"; 2="Alarm". | <enumeration>
| YES | Discrete Input | 2710 | n_PAR_FlowmeterTripAction.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2712 | n_PAR_FlowmeterTripAction.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2714 | n_PAR_FlowmeterTripAction.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2711 | n_PAR_FlowmeterTripAction.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2710 | n_PAR_FlowmeterTripAction.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2720 | n_PAR_FlowmeterTripDelay.CurrentValue | 2 | Integer | How long to ignore a low-flow signal from the flow meter before triggering an alarm or warning. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2720 | n_PAR_FlowmeterTripDelay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2722 | n_PAR_FlowmeterTripDelay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2724 | n_PAR_FlowmeterTripDelay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2721 | n_PAR_FlowmeterTripDelay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2720 | n_PAR_FlowmeterTripDelay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2730 | r_PAR_FlowmeterTripThreshold.CurrentValue | 2 | Floating point | Minimum flow required to not produce a low flow warning/alarm. This is the current value for this parameter used in operation of the unit. In units of gpm. | gpm
| YES | Discrete Input | 2730 | r_PAR_FlowmeterTripThreshold.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2732 | r_PAR_FlowmeterTripThreshold.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | gpm
| YES | Input Register | 2734 | r_PAR_FlowmeterTripThreshold.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | gpm
| YES | Discrete Input | 2731 | r_PAR_FlowmeterTripThreshold.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2730 | r_PAR_FlowmeterTripThreshold.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | gpm
| NO | Input Register | 2740 | n_PAR_HealthCV_HrsWrnThresh.CurrentValue | 2 | Integer | Not currently implemented. | hours
| NO | Discrete Input | 2740 | n_PAR_HealthCV_HrsWrnThresh.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2742 | n_PAR_HealthCV_HrsWrnThresh.Maximum | 2 | Integer | Not currently implemented. | hours
| NO | Input Register | 2744 | n_PAR_HealthCV_HrsWrnThresh.Minimum | 2 | Integer | Not currently implemented. | hours
| NO | Discrete Input | 2741 | n_PAR_HealthCV_HrsWrnThresh.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2740 | n_PAR_HealthCV_HrsWrnThresh.RemoteValue | 2 | Integer | Not currently implemented. | hours
| NO | Input Register | 2750 | n_PAR_HealthCV_OpsWrnThresh.CurrentValue | 2 | Integer | Not currently implemented. | operations
| NO | Discrete Input | 2750 | n_PAR_HealthCV_OpsWrnThresh.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2752 | n_PAR_HealthCV_OpsWrnThresh.Maximum | 2 | Integer | Not currently implemented. | operations
| NO | Input Register | 2754 | n_PAR_HealthCV_OpsWrnThresh.Minimum | 2 | Integer | Not currently implemented. | operations
| NO | Discrete Input | 2751 | n_PAR_HealthCV_OpsWrnThresh.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2750 | n_PAR_HealthCV_OpsWrnThresh.RemoteValue | 2 | Integer | Not currently implemented. | operations
| NO | Input Register | 2760 | n_PAR_HealthHeaterHrsWrnThresh.CurrentValue | 2 | Integer | Not currently implemented. | hours
| NO | Discrete Input | 2760 | n_PAR_HealthHeaterHrsWrnThresh.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2762 | n_PAR_HealthHeaterHrsWrnThresh.Maximum | 2 | Integer | Not currently implemented. | hours
| NO | Input Register | 2764 | n_PAR_HealthHeaterHrsWrnThresh.Minimum | 2 | Integer | Not currently implemented. | hours
| NO | Discrete Input | 2761 | n_PAR_HealthHeaterHrsWrnThresh.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2760 | n_PAR_HealthHeaterHrsWrnThresh.RemoteValue | 2 | Integer | Not currently implemented. | hours
| YES | Input Register | 2770 | n_PAR_HealthHeaterOpsWrnThresh.CurrentValue | 2 | Integer | Maximum number of heater contactor on/off operations before the user is prompted to replace it. This is the current value for this parameter used in operation of the unit. In units of operations. | operations
| YES | Discrete Input | 2770 | n_PAR_HealthHeaterOpsWrnThresh.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2772 | n_PAR_HealthHeaterOpsWrnThresh.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | operations
| YES | Input Register | 2774 | n_PAR_HealthHeaterOpsWrnThresh.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | operations
| YES | Discrete Input | 2771 | n_PAR_HealthHeaterOpsWrnThresh.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2770 | n_PAR_HealthHeaterOpsWrnThresh.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | operations
| NO | Input Register | 2780 | n_PAR_HealthPumpHrsWrnThresh.CurrentValue | 2 | Integer | Not currently implemented. | hours
| NO | Discrete Input | 2780 | n_PAR_HealthPumpHrsWrnThresh.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2782 | n_PAR_HealthPumpHrsWrnThresh.Maximum | 2 | Integer | Not currently implemented. | hours
| NO | Input Register | 2784 | n_PAR_HealthPumpHrsWrnThresh.Minimum | 2 | Integer | Not currently implemented. | hours
| NO | Discrete Input | 2781 | n_PAR_HealthPumpHrsWrnThresh.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2780 | n_PAR_HealthPumpHrsWrnThresh.RemoteValue | 2 | Integer | Not currently implemented. | hours
| NO | Input Register | 2790 | n_PAR_HealthPumpOpsWrnThresh.CurrentValue | 2 | Integer | Not currently implemented. | operations
| NO | Discrete Input | 2790 | n_PAR_HealthPumpOpsWrnThresh.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 2792 | n_PAR_HealthPumpOpsWrnThresh.Maximum | 2 | Integer | Not currently implemented. | operations
| NO | Input Register | 2794 | n_PAR_HealthPumpOpsWrnThresh.Minimum | 2 | Integer | Not currently implemented. | operations
| NO | Discrete Input | 2791 | n_PAR_HealthPumpOpsWrnThresh.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 2790 | n_PAR_HealthPumpOpsWrnThresh.RemoteValue | 2 | Integer | Not currently implemented. | operations
| YES | Input Register | 2800 | n_PAR_HealthHeaterMaxOpsPerHour.CurrentValue | 2 | Integer | Max heater contactor operations per hour, which will trigger an overuse warning if exceeded. This is the current value for this parameter used in operation of the unit. In units of operations/hr. | operations/hr
| YES | Discrete Input | 2800 | n_PAR_HealthHeaterMaxOpsPerHour.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2802 | n_PAR_HealthHeaterMaxOpsPerHour.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | operations/hr
| YES | Input Register | 2804 | n_PAR_HealthHeaterMaxOpsPerHour.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | operations/hr
| YES | Discrete Input | 2801 | n_PAR_HealthHeaterMaxOpsPerHour.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2800 | n_PAR_HealthHeaterMaxOpsPerHour.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | operations/hr
| YES | Input Register | 2810 | n_PAR_NetworkingBootupDelay.CurrentValue | 2 | Integer | Time to wait after bootup before declaring networking errors and/or timeouts. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2810 | n_PAR_NetworkingBootupDelay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2812 | n_PAR_NetworkingBootupDelay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2814 | n_PAR_NetworkingBootupDelay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2811 | n_PAR_NetworkingBootupDelay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2810 | n_PAR_NetworkingBootupDelay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2820 | n_PAR_NetworkModbusStation.CurrentValue | 2 | Integer | Sets the Modbus protocol station ID. This is the current value for this parameter used in operation of the unit. | N/A
| YES | Discrete Input | 2820 | n_PAR_NetworkModbusStation.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2822 | n_PAR_NetworkModbusStation.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | N/A
| YES | Input Register | 2824 | n_PAR_NetworkModbusStation.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | N/A
| YES | Discrete Input | 2821 | n_PAR_NetworkModbusStation.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2820 | n_PAR_NetworkModbusStation.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | N/A
| YES | Input Register | 2830 | n_PAR_NetworkTO.CurrentValue | 2 | Integer | Sets the Modbus protocol timeout. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 2830 | n_PAR_NetworkTO.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2832 | n_PAR_NetworkTO.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 2834 | n_PAR_NetworkTO.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 2831 | n_PAR_NetworkTO.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2830 | n_PAR_NetworkTO.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 2840 | n_PAR_NetworkType.CurrentValue | 2 | Integer | Active enumerated value: Bitmask: 00000000="None"; xxxxx1xx="Modbus-TCP Slave via Ethernet"; xxxx1xxx="Modbus-TCP Master via Ethernet"; xxx1xxxx="OPC-UA Client via Ethernet"; xx1xxxxx="OPC-UA Server via Ethernet"; x1xxxxxx="SPI". | <enumeration>
| YES | Discrete Input | 2840 | n_PAR_NetworkType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2842 | n_PAR_NetworkType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2844 | n_PAR_NetworkType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2841 | n_PAR_NetworkType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2840 | n_PAR_NetworkType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2850 | n_PAR_HeartbeatWarningAlarm.CurrentValue | 2 | Integer | Specifies the action that should be taken when the network heartbeat, once established, is lost. Enumerated value: 0="Nothing"; 1="Warning If Disc"; 2="Warning If Absent"; 3="Alarm If Disc"; 4="Alarm If Absent". | <enumeration>
| YES | Discrete Input | 2850 | n_PAR_HeartbeatWarningAlarm.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2852 | n_PAR_HeartbeatWarningAlarm.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2854 | n_PAR_HeartbeatWarningAlarm.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2851 | n_PAR_HeartbeatWarningAlarm.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2850 | n_PAR_HeartbeatWarningAlarm.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2860 | n_PAR_SetpointSource.CurrentValue | 2 | Integer | Determine the source of the temperature setpoint for the process loop control. Enumerated value: In parameter list: 0="Main"; 1="Alternative"; 2="Ramp/Soak"; 3="Analog Signal"; 4="Network"; 5="Main/Alt Toggle". On home screen: 0="Main Setpoint"; 1="Alt Setpoint"; 2="Ramp/Soak"; 3="Analog Setpoint"; 4="Network Setpoint" based on n_HD_EffectiveSetpointSource.. | <enumeration>
| YES | Discrete Input | 2860 | n_PAR_SetpointSource.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2862 | n_PAR_SetpointSource.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2864 | n_PAR_SetpointSource.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2861 | n_PAR_SetpointSource.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2860 | n_PAR_SetpointSource.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2870 | n_PAR_ProcessValueSource.CurrentValue | 2 | Integer | Determines what temperature measurement is used for the loop process value. Enumerated value: 0="To Process RTD"; 1="From Process RTD"; 2="Avg RTD"; 3="Remote RTD"; 4="Analog Signal"; 5="Network". | <enumeration>
| YES | Discrete Input | 2870 | n_PAR_ProcessValueSource.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2872 | n_PAR_ProcessValueSource.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 2874 | n_PAR_ProcessValueSource.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 2871 | n_PAR_ProcessValueSource.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2870 | n_PAR_ProcessValueSource.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 2880 | n_PAR_ProcessValueSmoothing.CurrentValue | 2 | Integer | How much smoothing to apply to the measured process temperature. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2880 | n_PAR_ProcessValueSmoothing.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2882 | n_PAR_ProcessValueSmoothing.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2884 | n_PAR_ProcessValueSmoothing.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2881 | n_PAR_ProcessValueSmoothing.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2880 | n_PAR_ProcessValueSmoothing.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2890 | n_PAR_DisplayPV_Smoothing.CurrentValue | 2 | Integer | How much smoothing to apply to the measured process temperature as displayed on the screen. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2890 | n_PAR_DisplayPV_Smoothing.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2892 | n_PAR_DisplayPV_Smoothing.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2894 | n_PAR_DisplayPV_Smoothing.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2891 | n_PAR_DisplayPV_Smoothing.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2890 | n_PAR_DisplayPV_Smoothing.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2900 | n_PAR_RampSoakPauseTO.CurrentValue | 2 | Integer | Exceeding this, while paused in Ramp/Soak due to low pressure, will abandon efforts for auto-restart. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2900 | n_PAR_RampSoakPauseTO.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2902 | n_PAR_RampSoakPauseTO.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2904 | n_PAR_RampSoakPauseTO.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2901 | n_PAR_RampSoakPauseTO.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2900 | n_PAR_RampSoakPauseTO.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 2910 | n_PAR_StartupIgnoreDevDelay.CurrentValue | 2 | Integer | How long to ignore temperature deviations after machine startup. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes
| YES | Discrete Input | 2910 | n_PAR_StartupIgnoreDevDelay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2912 | n_PAR_StartupIgnoreDevDelay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Input Register | 2914 | n_PAR_StartupIgnoreDevDelay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Discrete Input | 2911 | n_PAR_StartupIgnoreDevDelay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2910 | n_PAR_StartupIgnoreDevDelay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes
| YES | Input Register | 2920 | r_PAR_TempDev_OverSP.CurrentValue | 2 | Floating point | Process temperature over the setpoint necessary to trigger a high deviation alarm. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 2920 | r_PAR_TempDev_OverSP.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2922 | r_PAR_TempDev_OverSP.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 2924 | r_PAR_TempDev_OverSP.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 2921 | r_PAR_TempDev_OverSP.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2920 | r_PAR_TempDev_OverSP.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 2930 | r_PAR_TempDev_UnderSP.CurrentValue | 2 | Floating point | Process temperature under the setpoint necessary to trigger a low deviation alarm. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 2930 | r_PAR_TempDev_UnderSP.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2932 | r_PAR_TempDev_UnderSP.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 2934 | r_PAR_TempDev_UnderSP.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 2931 | r_PAR_TempDev_UnderSP.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2930 | r_PAR_TempDev_UnderSP.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 2940 | n_PAR_TempDev_OverSP_Delay.CurrentValue | 2 | Integer | How long to wait, if a high temperature deviation is detected, before triggering a warning/alarm. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes
| YES | Discrete Input | 2940 | n_PAR_TempDev_OverSP_Delay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2942 | n_PAR_TempDev_OverSP_Delay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Input Register | 2944 | n_PAR_TempDev_OverSP_Delay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Discrete Input | 2941 | n_PAR_TempDev_OverSP_Delay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2940 | n_PAR_TempDev_OverSP_Delay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes
| YES | Input Register | 2950 | n_PAR_TempDev_UnderSP_Delay.CurrentValue | 2 | Integer | How long to wait, if a low temperature deviation is detected, before triggering a warning/alarm. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes
| YES | Discrete Input | 2950 | n_PAR_TempDev_UnderSP_Delay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2952 | n_PAR_TempDev_UnderSP_Delay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Input Register | 2954 | n_PAR_TempDev_UnderSP_Delay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| YES | Discrete Input | 2951 | n_PAR_TempDev_UnderSP_Delay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2950 | n_PAR_TempDev_UnderSP_Delay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes
| YES | Input Register | 2960 | r_PAR_MainTempSetpoint.CurrentValue | 2 | Floating point | Main process temperature setpoint for the machine. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2960 | r_PAR_MainTempSetpoint.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2962 | r_PAR_MainTempSetpoint.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2964 | r_PAR_MainTempSetpoint.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2961 | r_PAR_MainTempSetpoint.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2960 | r_PAR_MainTempSetpoint.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2970 | r_PAR_AltTempSetpoint.CurrentValue | 2 | Floating point | Alternative process temperature setpoint for the machine. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2970 | r_PAR_AltTempSetpoint.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2972 | r_PAR_AltTempSetpoint.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2974 | r_PAR_AltTempSetpoint.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2971 | r_PAR_AltTempSetpoint.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2970 | r_PAR_AltTempSetpoint.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2980 | r_PAR_CooldownShutdownTemp.CurrentValue | 2 | Floating point | Temperature at which Auto Cool Stop is considered complete and the machine will shut down. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 2980 | r_PAR_CooldownShutdownTemp.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2982 | r_PAR_CooldownShutdownTemp.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 2984 | r_PAR_CooldownShutdownTemp.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 2981 | r_PAR_CooldownShutdownTemp.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2980 | r_PAR_CooldownShutdownTemp.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 2990 | r_PAR_CoolingCycleTime.CurrentValue | 2 | Floating point | The cooling valve cycle time, providing the PWM timebase for the cooling valve. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 2990 | r_PAR_CoolingCycleTime.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 2992 | r_PAR_CoolingCycleTime.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 2994 | r_PAR_CoolingCycleTime.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 2991 | r_PAR_CoolingCycleTime.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 2990 | r_PAR_CoolingCycleTime.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 3000 | r_PAR_CoolingMaxPWM.CurrentValue | 2 | Floating point | Maximum "on time" for the cooling valve. Requests above this will result in 100% cooling. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 3000 | r_PAR_CoolingMaxPWM.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3002 | r_PAR_CoolingMaxPWM.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 3004 | r_PAR_CoolingMaxPWM.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 3001 | r_PAR_CoolingMaxPWM.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3000 | r_PAR_CoolingMaxPWM.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 3010 | r_PAR_CoolingMinPWM.CurrentValue | 2 | Floating point | Minimum "on time" for the cooling valve. Requests below this will result in 0% cooling. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 3010 | r_PAR_CoolingMinPWM.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3012 | r_PAR_CoolingMinPWM.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 3014 | r_PAR_CoolingMinPWM.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 3011 | r_PAR_CoolingMinPWM.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3010 | r_PAR_CoolingMinPWM.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 3020 | r_PAR_HeatingCycleTime.CurrentValue | 2 | Floating point | The heater cycle time, providing the PWM timebase for the heater. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 3020 | r_PAR_HeatingCycleTime.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3022 | r_PAR_HeatingCycleTime.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 3024 | r_PAR_HeatingCycleTime.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 3021 | r_PAR_HeatingCycleTime.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3020 | r_PAR_HeatingCycleTime.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 3030 | r_PAR_HeatingMaxPWM.CurrentValue | 2 | Floating point | Maximum "on time" for the heater. Requests above this will result in 100% heating. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 3030 | r_PAR_HeatingMaxPWM.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3032 | r_PAR_HeatingMaxPWM.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 3034 | r_PAR_HeatingMaxPWM.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 3031 | r_PAR_HeatingMaxPWM.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3030 | r_PAR_HeatingMaxPWM.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 3040 | r_PAR_HeatingMinPWM.CurrentValue | 2 | Floating point | Minimum "on time" for the heater. Requests below this will result in 0% heating. This is the current value for this parameter used in operation of the unit. In units of %. | %
| YES | Discrete Input | 3040 | r_PAR_HeatingMinPWM.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3042 | r_PAR_HeatingMinPWM.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Input Register | 3044 | r_PAR_HeatingMinPWM.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| YES | Discrete Input | 3041 | r_PAR_HeatingMinPWM.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3040 | r_PAR_HeatingMinPWM.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | %
| YES | Input Register | 3050 | r_PAR_HeaterDeadband.CurrentValue | 2 | Floating point | Magnitude of dynamic heating deadband. (Will be active only when overall cooling is occurring.) This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3050 | r_PAR_HeaterDeadband.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3052 | r_PAR_HeaterDeadband.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3054 | r_PAR_HeaterDeadband.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3051 | r_PAR_HeaterDeadband.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3050 | r_PAR_HeaterDeadband.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| NO | Input Register | 3060 | n_PAR_AlgorithmType.CurrentValue | 2 | Integer | <enumeration> This is the current value for this parameter used in operation of the unit. | ---
| NO | Discrete Input | 3060 | n_PAR_AlgorithmType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| NO | Input Register | 3062 | n_PAR_AlgorithmType.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | ---
| NO | Input Register | 3064 | n_PAR_AlgorithmType.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | ---
| NO | Discrete Input | 3061 | n_PAR_AlgorithmType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| NO | Holding Register | 3060 | n_PAR_AlgorithmType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | ---
| YES | Input Register | 3070 | r_PAR_PID_P_Band.CurrentValue | 2 | Floating point | Temp band over which P-response will be 100%. Smaller value = more aggressive P-response. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3070 | r_PAR_PID_P_Band.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3072 | r_PAR_PID_P_Band.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3074 | r_PAR_PID_P_Band.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3071 | r_PAR_PID_P_Band.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3070 | r_PAR_PID_P_Band.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 3080 | r_PAR_PID_I_Gain.CurrentValue | 2 | Floating point | Temperature PID integral gain. Smaller value = more aggressive I-response, disabled with "0". This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 3080 | r_PAR_PID_I_Gain.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3082 | r_PAR_PID_I_Gain.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 3084 | r_PAR_PID_I_Gain.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 3081 | r_PAR_PID_I_Gain.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3080 | r_PAR_PID_I_Gain.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 3090 | r_PAR_PID_D_Gain.CurrentValue | 2 | Floating point | Temperature PID derivative gain. Larger value = more aggressive D-response, disabled with "0". This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds
| YES | Discrete Input | 3090 | r_PAR_PID_D_Gain.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3092 | r_PAR_PID_D_Gain.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 3094 | r_PAR_PID_D_Gain.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 3091 | r_PAR_PID_D_Gain.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3090 | r_PAR_PID_D_Gain.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Input Register | 3100 | r_PAR_PID_Deadband.CurrentValue | 2 | Floating point | Output deadband for the PID function. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3100 | r_PAR_PID_Deadband.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3102 | r_PAR_PID_Deadband.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3104 | r_PAR_PID_Deadband.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3101 | r_PAR_PID_Deadband.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3100 | r_PAR_PID_Deadband.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 3110 | r_PAR_PID_IntegralActiveBand.CurrentValue | 2 | Floating point | Temperature band over which the PID integral response is active. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3110 | r_PAR_PID_IntegralActiveBand.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3112 | r_PAR_PID_IntegralActiveBand.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3114 | r_PAR_PID_IntegralActiveBand.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3111 | r_PAR_PID_IntegralActiveBand.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3110 | r_PAR_PID_IntegralActiveBand.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 3120 | r_PAR_PID_DynamicHeatRatioMult.CurrentValue | 2 | Floating point | Characterizes the thermal power of cooling vs heating when operating at high process temperatures. This is the current value for this parameter used in operation of the unit. | ---
| YES | Discrete Input | 3120 | r_PAR_PID_DynamicHeatRatioMult.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3122 | r_PAR_PID_DynamicHeatRatioMult.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | ---
| YES | Input Register | 3124 | r_PAR_PID_DynamicHeatRatioMult.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | ---
| YES | Discrete Input | 3121 | r_PAR_PID_DynamicHeatRatioMult.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3120 | r_PAR_PID_DynamicHeatRatioMult.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | ---
| YES | Input Register | 3130 | r_PAR_PID_HeatToCoolOutRatio.CurrentValue | 2 | Floating point | Value of 1.0=equal heating/cooling. Values <1.0 for large heaters. Values >1.0 for small heaters. This is the current value for this parameter used in operation of the unit. | ---
| YES | Discrete Input | 3130 | r_PAR_PID_HeatToCoolOutRatio.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3132 | r_PAR_PID_HeatToCoolOutRatio.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | ---
| YES | Input Register | 3134 | r_PAR_PID_HeatToCoolOutRatio.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | ---
| YES | Discrete Input | 3131 | r_PAR_PID_HeatToCoolOutRatio.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3130 | r_PAR_PID_HeatToCoolOutRatio.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | ---
| YES | Input Register | 3140 | r_PAR_ProcessDB_Threshold.CurrentValue | 2 | Floating point | Magnitude of accumulated process cooling that is required to enable heating deadbanding. This is the current value for this parameter used in operation of the unit. In units of Δ°C·sec. | Δ°C<dot>sec
| YES | Discrete Input | 3140 | r_PAR_ProcessDB_Threshold.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3142 | r_PAR_ProcessDB_Threshold.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C<dot>sec
| YES | Input Register | 3144 | r_PAR_ProcessDB_Threshold.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C<dot>sec
| YES | Discrete Input | 3141 | r_PAR_ProcessDB_Threshold.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3140 | r_PAR_ProcessDB_Threshold.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C<dot>sec
| YES | Input Register | 3150 | r_PAR_SupplyRTD_CalOffset.CurrentValue | 2 | Floating point | Defines a calibration offset for the "To Process" RTD temperature sensor. This is the current value for this parameter used in operation of the unit. in units of Δ°C. | Δ°C
| YES | Discrete Input | 3150 | r_PAR_SupplyRTD_CalOffset.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3152 | r_PAR_SupplyRTD_CalOffset.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3154 | r_PAR_SupplyRTD_CalOffset.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3151 | r_PAR_SupplyRTD_CalOffset.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3150 | r_PAR_SupplyRTD_CalOffset.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 3160 | r_PAR_ReturnRTD_CalOffset.CurrentValue | 2 | Floating point | Defines a calibration offset for the "From Process" RTD temperature sensor. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3160 | r_PAR_ReturnRTD_CalOffset.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3162 | r_PAR_ReturnRTD_CalOffset.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3164 | r_PAR_ReturnRTD_CalOffset.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3161 | r_PAR_ReturnRTD_CalOffset.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3160 | r_PAR_ReturnRTD_CalOffset.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 3170 | r_PAR_RemoteRTD_CalOffset.CurrentValue | 2 | Floating point | Defines a calibration offset for the Remote RTD temperature sensor. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3170 | r_PAR_RemoteRTD_CalOffset.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3172 | r_PAR_RemoteRTD_CalOffset.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3174 | r_PAR_RemoteRTD_CalOffset.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3171 | r_PAR_RemoteRTD_CalOffset.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3170 | r_PAR_RemoteRTD_CalOffset.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| NO | Input Register | 3180 | r_PAR_NetworkProcessCalOffset.CurrentValue | 2 | Floating point | Not currently implemented. | Δ°C
| NO | Discrete Input | 3180 | r_PAR_NetworkProcessCalOffset.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 3182 | r_PAR_NetworkProcessCalOffset.Maximum | 2 | Floating point | Not currently implemented. | Δ°C
| NO | Input Register | 3184 | r_PAR_NetworkProcessCalOffset.Minimum | 2 | Floating point | Not currently implemented. | Δ°C
| NO | Discrete Input | 3181 | r_PAR_NetworkProcessCalOffset.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 3180 | r_PAR_NetworkProcessCalOffset.RemoteValue | 2 | Floating point | Not currently implemented. | Δ°C
| YES | Input Register | 3190 | r_PAR_TwoWireRTD_Offset.CurrentValue | 2 | Floating point | Defines a calibration offset on 2-wire RTD temperature sensors to compensate for lead resistance. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3190 | r_PAR_TwoWireRTD_Offset.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3192 | r_PAR_TwoWireRTD_Offset.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3194 | r_PAR_TwoWireRTD_Offset.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3191 | r_PAR_TwoWireRTD_Offset.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3190 | r_PAR_TwoWireRTD_Offset.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 3200 | r_PAR_UserTempHighAlarm.CurrentValue | 2 | Floating point | Temperature above which an operator-defined high-temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 3200 | r_PAR_UserTempHighAlarm.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3202 | r_PAR_UserTempHighAlarm.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 3204 | r_PAR_UserTempHighAlarm.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 3201 | r_PAR_UserTempHighAlarm.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3200 | r_PAR_UserTempHighAlarm.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 3210 | r_PAR_UserTempLowAlarm.CurrentValue | 2 | Floating point | Temperature under which an operator-defined low-temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 3210 | r_PAR_UserTempLowAlarm.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3212 | r_PAR_UserTempLowAlarm.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 3214 | r_PAR_UserTempLowAlarm.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 3211 | r_PAR_UserTempLowAlarm.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3210 | r_PAR_UserTempLowAlarm.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 3220 | n_PAR_FluidType.CurrentValue | 2 | Integer | Selects whether the process is using pure water or a water/glycol mix. Enumerated value: 0=Water; 1=25% Ethylene Glycol/75% Water; 2=50% Ethylene Glycol/75% Water. | <enumeration>
| YES | Discrete Input | 3220 | n_PAR_FluidType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3222 | n_PAR_FluidType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 3224 | n_PAR_FluidType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 3221 | n_PAR_FluidType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3220 | n_PAR_FluidType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 3230 | r_PAR_PlumbingCv.CurrentValue | 2 | Floating point | Cv of the connected facility plumbing. Anything greater than 100 is considered negligible. This is the current value for this parameter used in operation of the unit. In units of gal/min/psi. | gal/min/psi
| YES | Discrete Input | 3230 | r_PAR_PlumbingCv.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3232 | r_PAR_PlumbingCv.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | gal/min/psi
| YES | Input Register | 3234 | r_PAR_PlumbingCv.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | gal/min/psi
| YES | Discrete Input | 3231 | r_PAR_PlumbingCv.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3230 | r_PAR_PlumbingCv.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | gal/min/psi
| YES | Input Register | 3240 | n_PAR_Language.CurrentValue | 2 | Integer | Language selection for touchscreen. Enumerated value: 0="English". | <enumeration>
| YES | Discrete Input | 3240 | n_PAR_Language.Implemented | 1 | Bool | Currently only 1 setting (English) | Yes/No
| YES | Input Register | 3242 | n_PAR_Language.Maximum | 2 | Integer | Currently only 1 setting (English) | <enumeration>
| YES | Input Register | 3244 | n_PAR_Language.Minimum | 2 | Integer | Currently only 1 setting (English) | <enumeration>
| YES | Discrete Input | 3241 | n_PAR_Language.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3240 | n_PAR_Language.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 3250 | r_PAR_MaxPanelTemp.CurrentValue | 2 | Floating point | Temperature above which an electrical panel high temperature alarm will be triggered. This is the current value for this parameter used in operation of the unit. In units of °C. | °C
| YES | Discrete Input | 3250 | r_PAR_MaxPanelTemp.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3252 | r_PAR_MaxPanelTemp.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Input Register | 3254 | r_PAR_MaxPanelTemp.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| YES | Discrete Input | 3251 | r_PAR_MaxPanelTemp.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3250 | r_PAR_MaxPanelTemp.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C
| YES | Input Register | 3260 | r_PAR_EnclosureTempOffset.CurrentValue | 2 | Floating point | Difference between temperature sensor and the actual electrical enclosure ambient temperature. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C
| YES | Discrete Input | 3260 | r_PAR_EnclosureTempOffset.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3262 | r_PAR_EnclosureTempOffset.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Input Register | 3264 | r_PAR_EnclosureTempOffset.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| YES | Discrete Input | 3261 | r_PAR_EnclosureTempOffset.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3260 | r_PAR_EnclosureTempOffset.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C
| YES | Input Register | 3270 | r_PAR_MaxPressure.CurrentValue | 2 | Floating point | From-process pressure above this value will trigger a high-pressure alarm. This is the current value for this parameter used in operation of the unit. In units of psi. | psi
| YES | Discrete Input | 3270 | r_PAR_MaxPressure.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3272 | r_PAR_MaxPressure.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | psi
| YES | Input Register | 3274 | r_PAR_MaxPressure.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | psi
| YES | Discrete Input | 3271 | r_PAR_MaxPressure.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3270 | r_PAR_MaxPressure.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | psi
| YES | Input Register | 3280 | r_PAR_AutoHotPressureReliefPress.CurrentValue | 2 | Floating point | Pressure at which the automatic hot pressure relief will be triggered. This is the current value for this parameter used in operation of the unit. In units of pounds per square inch (psi). | psi
| YES | Discrete Input | 3280 | r_PAR_AutoHotPressureReliefPress.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3282 | r_PAR_AutoHotPressureReliefPress.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | psi
| YES | Input Register | 3284 | r_PAR_AutoHotPressureReliefPress.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | psi
| YES | Discrete Input | 3281 | r_PAR_AutoHotPressureReliefPress.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3280 | r_PAR_AutoHotPressureReliefPress.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | psi
| YES | Input Register | 3290 | r_PAR_SoftwareVersion.CurrentValue | 2 | Floating point | Application software version. This is the current value for this parameter used in operation of the unit. | N/A
| YES | Discrete Input | 3290 | r_PAR_SoftwareVersion.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3292 | r_PAR_SoftwareVersion.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | N/A
| YES | Input Register | 3294 | r_PAR_SoftwareVersion.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | N/A
| YES | Discrete Input | 3291 | r_PAR_SoftwareVersion.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3290 | r_PAR_SoftwareVersion.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | N/A
| NO | Input Register | 3300 | r_PAR_PID_AT_ControlOutputLimit.CurrentValue | 2 | Floating point | Not currently implemented. | %
| NO | Discrete Input | 3300 | r_PAR_PID_AT_ControlOutputLimit.Implemented | 1 | Bool | Not currently implemented | Yes/No
| NO | Input Register | 3302 | r_PAR_PID_AT_ControlOutputLimit.Maximum | 2 | Floating point | Not currently implemented | %
| NO | Input Register | 3304 | r_PAR_PID_AT_ControlOutputLimit.Minimum | 2 | Floating point | Not currently implemented | %
| NO | Discrete Input | 3301 | r_PAR_PID_AT_ControlOutputLimit.RemoteWriteAccess | 1 | Bool | Not currently implemented | Yes/No
| NO | Holding Register | 3300 | r_PAR_PID_AT_ControlOutputLimit.RemoteValue | 2 | Floating point | Not currently implemented | %
| NO | Input Register | 3310 | r_PAR_PID_AT_ControlStepChange.CurrentValue | 2 | Floating point | Not currently implemented | %
| NO | Discrete Input | 3310 | r_PAR_PID_AT_ControlStepChange.Implemented | 1 | Bool | Not currently implemented | Yes/No
| NO | Input Register | 3312 | r_PAR_PID_AT_ControlStepChange.Maximum | 2 | Floating point | Not currently implemented | %
| NO | Input Register | 3314 | r_PAR_PID_AT_ControlStepChange.Minimum | 2 | Floating point | Not currently implemented | %
| NO | Discrete Input | 3311 | r_PAR_PID_AT_ControlStepChange.RemoteWriteAccess | 1 | Bool | Not currently implemented | Yes/No
| NO | Holding Register | 3310 | r_PAR_PID_AT_ControlStepChange.RemoteValue | 2 | Floating point | Not currently implemented | %
| NO | Input Register | 3320 | r_PAR_PID_AT_LambdaMultiplier.CurrentValue | 2 | Floating point | Not currently implemented | N/A
| NO | Discrete Input | 3320 | r_PAR_PID_AT_LambdaMultiplier.Implemented | 1 | Bool | Not currently implemented | Yes/No
| NO | Input Register | 3322 | r_PAR_PID_AT_LambdaMultiplier.Maximum | 2 | Floating point | Not currently implemented | N/A
| NO | Input Register | 3324 | r_PAR_PID_AT_LambdaMultiplier.Minimum | 2 | Floating point | Not currently implemented | N/A
| NO | Discrete Input | 3321 | r_PAR_PID_AT_LambdaMultiplier.RemoteWriteAccess | 1 | Bool | Not currently implemented | Yes/No
| NO | Holding Register | 3320 | r_PAR_PID_AT_LambdaMultiplier.RemoteValue | 2 | Floating point | Not currently implemented | N/A
| NO | Input Register | 3330 | r_PAR_PID_AT_Deadband.CurrentValue | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3330 | r_PAR_PID_AT_Deadband.Implemented | 1 | Bool | Not currently implemented | Yes/No
| NO | Input Register | 3332 | r_PAR_PID_AT_Deadband.Maximum | 2 | Floating point | Not currently implemented | °C
| NO | Input Register | 3334 | r_PAR_PID_AT_Deadband.Minimum | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3331 | r_PAR_PID_AT_Deadband.RemoteWriteAccess | 1 | Bool | Not currently implemented | Yes/No
| NO | Holding Register | 3330 | r_PAR_PID_AT_Deadband.RemoteValue | 2 | Floating point | Not currently implemented | °C
| NO | Input Register | 3340 | r_PAR_PID_AT_MinProcValueAt0.CurrentValue | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3340 | r_PAR_PID_AT_MinProcValueAt0.Implemented | 1 | Bool | Not currently implemented | Yes/No
| NO | Input Register | 3342 | r_PAR_PID_AT_MinProcValueAt0.Maximum | 2 | Floating point | Not currently implemented | °C
| NO | Input Register | 3344 | r_PAR_PID_AT_MinProcValueAt0.Minimum | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3341 | r_PAR_PID_AT_MinProcValueAt0.RemoteWriteAccess | 1 | Bool | Not currently implemented | Yes/No
| NO | Holding Register | 3340 | r_PAR_PID_AT_MinProcValueAt0.RemoteValue | 2 | Floating point | Not currently implemented | °C
| NO | Input Register | 3350 | r_PAR_PID_AT_MaxProcValueAt100.CurrentValue | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3350 | r_PAR_PID_AT_MaxProcValueAt100.Implemented | 1 | Bool | Not currently implemented | Yes/No
| NO | Input Register | 3352 | r_PAR_PID_AT_MaxProcValueAt100.Maximum | 2 | Floating point | Not currently implemented | °C
| NO | Input Register | 3354 | r_PAR_PID_AT_MaxProcValueAt100.Minimum | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3351 | r_PAR_PID_AT_MaxProcValueAt100.RemoteWriteAccess | 1 | Bool | Not currently implemented | Yes/No
| NO | Holding Register | 3350 | r_PAR_PID_AT_MaxProcValueAt100.RemoteValue | 2 | Floating point | Not currently implemented | °C
| NO | Input Register | 3360 | r_PAR_PID_AT_ProcessValueLimit.CurrentValue | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3360 | r_PAR_PID_AT_ProcessValueLimit.Implemented | 1 | Bool | Not currently implemented | Yes/No
| NO | Input Register | 3362 | r_PAR_PID_AT_ProcessValueLimit.Maximum | 2 | Floating point | Not currently implemented | °C
| NO | Input Register | 3364 | r_PAR_PID_AT_ProcessValueLimit.Minimum | 2 | Floating point | Not currently implemented | °C
| NO | Discrete Input | 3361 | r_PAR_PID_AT_ProcessValueLimit.RemoteWriteAccess | 1 | Bool | Not currently implemented | Yes/No
| NO | Holding Register | 3360 | r_PAR_PID_AT_ProcessValueLimit.RemoteValue | 2 | Floating point | Not currently implemented | °C
| YES | Input Register | 3370 | r_PAR_HotPressReliefAnticipate.CurrentValue | 2 | Floating point | How far below the hot pressure relief threshold to anticipate the need to automatically relieve. This is the current value for this parameter used in operation of the unit. In units of Δpsi. | Δpsi
| YES | Discrete Input | 3370 | r_PAR_HotPressReliefAnticipate.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3372 | r_PAR_HotPressReliefAnticipate.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| YES | Input Register | 3374 | r_PAR_HotPressReliefAnticipate.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| YES | Discrete Input | 3371 | r_PAR_HotPressReliefAnticipate.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3370 | r_PAR_HotPressReliefAnticipate.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δpsi
| YES | Input Register | 3380 | r_PAR_HotPressReliefHysteresis.CurrentValue | 2 | Floating point | How much pressure drop is required during hot pressure relief to consider the relief complete. This is the current value for this parameter used in operation of the unit. In units of Δpsi. | Δpsi
| YES | Discrete Input | 3380 | r_PAR_HotPressReliefHysteresis.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3382 | r_PAR_HotPressReliefHysteresis.Maximum | 2 | Floating point | The maximum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| YES | Input Register | 3384 | r_PAR_HotPressReliefHysteresis.Minimum | 2 | Floating point | The minimum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| YES | Discrete Input | 3381 | r_PAR_HotPressReliefHysteresis.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3380 | r_PAR_HotPressReliefHysteresis.RemoteValue | 2 | Floating point | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δpsi
| YES | Input Register | 3390 | n_PAR_NetworkSpi485Baudrate.CurrentValue | 2 | Integer | Sets the SPI via RS-485 protocol baud rate. Enumerated value: 1="2400 bps"; 2="4800 bps"; 3="9600 bps"; 4="19200 bps"; 5="38400 bps"; 7="57600 bps"; 8="115200 bps" (there is no valid speed for "6").. | <enumeration>
| YES | Discrete Input | 3390 | n_PAR_NetworkSpi485Baudrate.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3392 | n_PAR_NetworkSpi485Baudrate.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 3394 | n_PAR_NetworkSpi485Baudrate.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 3391 | n_PAR_NetworkSpi485Baudrate.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3390 | n_PAR_NetworkSpi485Baudrate.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 3400 | n_PAR_NetworkSpiStation.CurrentValue | 2 | Integer | Sets the SPI protocol device address. This decimal value is added to the default device address of 20 hex (32 decimal). This is the current value for this parameter used in operation of the unit. | <enumeration>
| YES | Discrete Input | 3400 | n_PAR_NetworkSpiStation.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3402 | n_PAR_NetworkSpiStation.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 3404 | n_PAR_NetworkSpiStation.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 3401 | n_PAR_NetworkSpiStation.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3400 | n_PAR_NetworkSpiStation.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Discrete Input | 3410 | b_PAR_EstimatedFlowrateEnable.CurrentValue | 1 | Bool | Enables the calculation of estimated flow from the differential pressure across the pump. Enumerated value: FALSE=Estimated flowrate calculation disabled.; TRUE=Estimated flowrate calculation enabled. | <enumeration>
| YES | Discrete Input | 3411 | b_PAR_EstimatedFlowrateEnable.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 3412 | b_PAR_EstimatedFlowrateEnable.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 3410 | b_PAR_EstimatedFlowrateEnable.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 3420 | b_PAR_DHCP_Enable.CurrentValue | 1 | Bool | Enables dynamic IP address assignment. Enumerated value: FALSE=DHCP disabled (static IP addresses); TRUE=DHCP enabled (dynamic IP addresses). | <enumeration>
| YES | Discrete Input | 3421 | b_PAR_DHCP_Enable.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 3422 | b_PAR_DHCP_Enable.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 3420 | b_PAR_DHCP_Enable.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 3430 | n_PAR_PumpType.CurrentValue | 2 | Integer | Sets the pump manufacturer. Important for estimated flow due to different flow curves. Enumerated value: 0="Not Selected", 1="Type X", 2="Type S". | <enumeration>
| YES | Discrete Input | 3430 | n_PAR_PumpType.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3432 | n_PAR_PumpType.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 3434 | n_PAR_PumpType.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 3431 | n_PAR_PumpType.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3430 | n_PAR_PumpType.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 3440 | n_PAR_PostMoldPurgeBleedDown.CurrentValue | 2 | Integer | Time cooling valve should remain open after mold purge is complete to bleed out residual pressure. This is the current value for this parameter used in operation of the unit. | seconds
| YES | Discrete Input | 3440 | n_PAR_PostMoldPurgeBleedDown.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3442 | n_PAR_PostMoldPurgeBleedDown.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 3444 | n_PAR_PostMoldPurgeBleedDown.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 3441 | n_PAR_PostMoldPurgeBleedDown.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3440 | n_PAR_PostMoldPurgeBleedDown.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Discrete Input | 3450 | b_PAR_BankingInstalled.CurrentValue | 1 | Bool | Is the ability to do multi-unit banking permitted? Enumerated value: FALSE=Banking Not Permitted; TRUE=Banking Permitted. | <enumeration>
| YES | Discrete Input | 3451 | b_PAR_BankingInstalled.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 3452 | b_PAR_BankingInstalled.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 3450 | b_PAR_BankingInstalled.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Input Register | 3460 | n_PAR_BankingNodes.CurrentValue | 2 | Integer | Number of units in the bank (including the master). This is the current value for this parameter used in operation of the unit. In units of units. | units
| YES | Discrete Input | 3460 | n_PAR_BankingNodes.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3462 | n_PAR_BankingNodes.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | units
| YES | Input Register | 3464 | n_PAR_BankingNodes.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | units
| YES | Discrete Input | 3461 | n_PAR_BankingNodes.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3460 | n_PAR_BankingNodes.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | units
| YES | Input Register | 3470 | n_PAR_BankAlarmsAction.CurrentValue | 2 | Integer | Determines how the master should inherit warnings or alarms from the slaves in the bank. Enumerated value: 0="Inherit nothing", 1="Inherit Remote Warnings Only", 2="Inherit Remote Alarms Only", 3="Inherit Both Remote Warnings and Alarms".. | <enumeration>
| YES | Discrete Input | 3470 | n_PAR_BankAlarmsAction.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3472 | n_PAR_BankAlarmsAction.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 3474 | n_PAR_BankAlarmsAction.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 3471 | n_PAR_BankAlarmsAction.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3470 | n_PAR_BankAlarmsAction.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 3480 | n_PAR_BankingPollInterval.CurrentValue | 2 | Integer | How often to poll the bank slaves for status and update their operations. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 3480 | n_PAR_BankingPollInterval.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3482 | n_PAR_BankingPollInterval.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 3484 | n_PAR_BankingPollInterval.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 3481 | n_PAR_BankingPollInterval.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3480 | n_PAR_BankingPollInterval.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 3490 | n_PAR_BankedPumpStartupInterval.CurrentValue | 2 | Integer | Interval between sequential pump starts in a bank. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds
| YES | Discrete Input | 3490 | n_PAR_BankedPumpStartupInterval.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3492 | n_PAR_BankedPumpStartupInterval.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Input Register | 3494 | n_PAR_BankedPumpStartupInterval.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| YES | Discrete Input | 3491 | n_PAR_BankedPumpStartupInterval.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3490 | n_PAR_BankedPumpStartupInterval.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds
| YES | Input Register | 3500 | n_PAR_HeatDistributedPowerMode.CurrentValue | 2 | Integer | How to sequence/time heating operations across a bank of units. Enumerated value: 0="Equally Shared, Inverted Timebases", 1="Equally Shared, NonInverted Timebases", 2="Progressive, Sequential Leader", 3="Progressive, First Unit Leading", 4="Progressive, Last Unit Leading".. | <enumeration>
| YES | Discrete Input | 3500 | n_PAR_HeatDistributedPowerMode.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3502 | n_PAR_HeatDistributedPowerMode.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 3504 | n_PAR_HeatDistributedPowerMode.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 3501 | n_PAR_HeatDistributedPowerMode.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3500 | n_PAR_HeatDistributedPowerMode.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 3510 | n_PAR_CoolDistributedPowerMode.CurrentValue | 2 | Integer | How to sequence/time cooling operations across a bank of units. Enumerated value: 0="Equally Shared" (mod valve), 0="Equally Shared, Inverted Timebases" (solenoid valve), 1="Equally Shared, NonInverted Timebases" (solenoid valve only), 2="Progressive, Sequential Leader", 3="Progressive, First Unit Leading", 4="Progressive, Last Unit Leading". | <enumeration>
| YES | Discrete Input | 3510 | n_PAR_CoolDistributedPowerMode.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3512 | n_PAR_CoolDistributedPowerMode.Maximum | 2 | Integer | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Input Register | 3514 | n_PAR_CoolDistributedPowerMode.Minimum | 2 | Integer | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| YES | Discrete Input | 3511 | n_PAR_CoolDistributedPowerMode.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3510 | n_PAR_CoolDistributedPowerMode.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration>
| YES | Input Register | 3520 | n_PAR_PumpRepetitiveStartDelay.CurrentValue | 2 | Integer | How long to wait between repetitive starts of the pump motor. This is the current value for this parameter used in operation of the unit. | seconds
| YES | Discrete Input | 3520 | n_PAR_PumpRepetitiveStartDelay.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 3522 | n_PAR_PumpRepetitiveStartDelay.Maximum | 2 | Integer | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Input Register | 3524 | n_PAR_PumpRepetitiveStartDelay.Minimum | 2 | Integer | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| YES | Discrete Input | 3521 | n_PAR_PumpRepetitiveStartDelay.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 3520 | n_PAR_PumpRepetitiveStartDelay.RemoteValue | 2 | Integer | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds
| YES | Discrete Input | 3530 | b_PAR_EnableAutoMoldPurge.CurrentValue | 1 | Bool | Mold purge cycle is automatically performed upon receiving a STOP signal. If b_PAR_EnableAutoCooldown is also enabled, it will occur first, then mold purge. Enumerated value: FALSE=Mold Purge At Shutdown Not Enabled; TRUE=Mold Purge At Shutdown Enabled. | <enumeration>
| YES | Discrete Input | 3531 | b_PAR_EnableAutoMoldPurge.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 3532 | b_PAR_EnableAutoMoldPurge.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 3530 | b_PAR_EnableAutoMoldPurge.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 3540 | b_PAR_EnableAutoCooldown.CurrentValue | 1 | Bool | Cooldown cycle is automatically performed upon receiving a STOP signal. Enumerated value: FALSE=Auto Cool Stop At Shutdown Not Enabled; TRUE=Auto Cool Stop At Shutdown Enabled. | <enumeration>
| YES | Discrete Input | 3541 | b_PAR_EnableAutoCooldown.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 3542 | b_PAR_EnableAutoCooldown.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 3540 | b_PAR_EnableAutoCooldown.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
| YES | Discrete Input | 3550 | b_PAR_OEM_Product.CurrentValue | 1 | Bool | Hides logo and all traces of branding for OEM use. Enumerated value: FALSE=Not an OEM product; TRUE=It is an OEM product.. | <enumeration>
| YES | Discrete Input | 3551 | b_PAR_OEM_Product.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 3552 | b_PAR_OEM_Product.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Coil | 3550 | b_PAR_OEM_Product.RemoteValue | 1 | Bool | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No
Analog Calibration Parameters, intended for individual read and writing only as necessary.
| YES | Input Register | 4000 | r_PARS_ModulatingCoolingValve.CurrentValueX1 | 2 | Floating point | Controller-produced % open that will correspond to the voltage given by Y1, in units of percent (%). | %
| YES | Input Register | 4002 | r_PARS_ModulatingCoolingValve.CurrentValueX2 | 2 | Floating point | Controller-produced %-open that will correspond to the voltage given by Y2, in units of percent (%). | %
| YES | Input Register | 4004 | r_PARS_ModulatingCoolingValve.CurrentValueY1 | 2 | Floating point | The voltage output that corresponds to the % open amount given by X1, in units of volts (V). | V
| YES | Input Register | 4006 | r_PARS_ModulatingCoolingValve.CurrentValueY2 | 2 | Floating point | The voltage output that corresponds to the % open amount given by X2, in units of volts (V). | V
| YES | Discrete Input | 4000 | r_PARS_ModulatingCoolingValve.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 4008 | r_PARS_ModulatingCoolingValve.MaximumX1 | 2 | Floating point | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of percent (%). | %
| YES | Input Register | 4010 | r_PARS_ModulatingCoolingValve.MaximumX2 | 2 | Floating point | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of percent (%). | %
| YES | Input Register | 4012 | r_PARS_ModulatingCoolingValve.MaximumY1 | 2 | Floating point | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V). | V
| YES | Input Register | 4014 | r_PARS_ModulatingCoolingValve.MaximumY2 | 2 | Floating point | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V). | V
| YES | Input Register | 4016 | r_PARS_ModulatingCoolingValve.MinimumX1 | 2 | Floating point | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of percent (%). | %
| YES | Input Register | 4018 | r_PARS_ModulatingCoolingValve.MinimumX2 | 2 | Floating point | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of percent (%). | %
| YES | Input Register | 4020 | r_PARS_ModulatingCoolingValve.MinimumY1 | 2 | Floating point | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V). | V
| YES | Input Register | 4022 | r_PARS_ModulatingCoolingValve.MinimumY2 | 2 | Floating point | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V). | V
| YES | Discrete Input | 4001 | r_PARS_ModulatingCoolingValve.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 4000 | r_PARS_ModulatingCoolingValve.RemoteValueX1 | 2 | Floating point | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of percent (%). | %
| YES | Holding Register | 4002 | r_PARS_ModulatingCoolingValve.RemoteValueX2 | 2 | Floating point | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of percent (%). | %
| YES | Holding Register | 4004 | r_PARS_ModulatingCoolingValve.RemoteValueY1 | 2 | Floating point | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of volts (V). | V
| YES | Holding Register | 4006 | r_PARS_ModulatingCoolingValve.RemoteValueY2 | 2 | Floating point | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of volts (V). | V
| YES | Input Register | 4100 | r_PARS_SupplyPressure.CurrentValueX1 | 2 | Floating point | Transducer-produced current that will correspond to the pressure given by Y1, in units of milliamps (mA). | mA
| YES | Input Register | 4102 | r_PARS_SupplyPressure.CurrentValueX2 | 2 | Floating point | Transducer-produced current that will correspond to the pressure given by Y2, in units of milliamps (mA). | mA
| YES | Input Register | 4104 | r_PARS_SupplyPressure.CurrentValueY1 | 2 | Floating point | Pressure that will correspond to the current specified by X1, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4106 | r_PARS_SupplyPressure.CurrentValueY2 | 2 | Floating point | Pressure that will correspond to the current specified by X2, in units of pounds per square inch (psi). | psi
| YES | Discrete Input | 4100 | r_PARS_SupplyPressure.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 4108 | r_PARS_SupplyPressure.MaximumX1 | 2 | Floating point | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| YES | Input Register | 4110 | r_PARS_SupplyPressure.MaximumX2 | 2 | Floating point | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| YES | Input Register | 4112 | r_PARS_SupplyPressure.MaximumY1 | 2 | Floating point | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4114 | r_PARS_SupplyPressure.MaximumY2 | 2 | Floating point | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4116 | r_PARS_SupplyPressure.MinimumX1 | 2 | Floating point | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| YES | Input Register | 4118 | r_PARS_SupplyPressure.MinimumX2 | 2 | Floating point | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| YES | Input Register | 4120 | r_PARS_SupplyPressure.MinimumY1 | 2 | Floating point | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4122 | r_PARS_SupplyPressure.MinimumY2 | 2 | Floating point | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| YES | Discrete Input | 4101 | r_PARS_SupplyPressure.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 4100 | r_PARS_SupplyPressure.RemoteValueX1 | 2 | Floating point | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA
| YES | Holding Register | 4102 | r_PARS_SupplyPressure.RemoteValueX2 | 2 | Floating point | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA
| YES | Holding Register | 4104 | r_PARS_SupplyPressure.RemoteValueY1 | 2 | Floating point | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi
| YES | Holding Register | 4106 | r_PARS_SupplyPressure.RemoteValueY2 | 2 | Floating point | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4200 | r_PARS_ReturnPressure.CurrentValueX1 | 2 | Floating point | Transducer-produced current that will correspond to the pressure given by Y1, in units of milliamps (mA). | mA
| YES | Input Register | 4202 | r_PARS_ReturnPressure.CurrentValueX2 | 2 | Floating point | Transducer-produced current that will correspond to the pressure given by Y2, in units of milliamps (mA). | mA
| YES | Input Register | 4204 | r_PARS_ReturnPressure.CurrentValueY1 | 2 | Floating point | Pressure that will correspond to the current specified by X1, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4206 | r_PARS_ReturnPressure.CurrentValueY2 | 2 | Floating point | Pressure that will correspond to the current specified by X2, in units of pounds per square inch (psi). | psi
| YES | Discrete Input | 4200 | r_PARS_ReturnPressure.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 4208 | r_PARS_ReturnPressure.MaximumX1 | 2 | Floating point | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| YES | Input Register | 4210 | r_PARS_ReturnPressure.MaximumX2 | 2 | Floating point | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| YES | Input Register | 4212 | r_PARS_ReturnPressure.MaximumY1 | 2 | Floating point | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4214 | r_PARS_ReturnPressure.MaximumY2 | 2 | Floating point | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4216 | r_PARS_ReturnPressure.MinimumX1 | 2 | Floating point | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| YES | Input Register | 4218 | r_PARS_ReturnPressure.MinimumX2 | 2 | Floating point | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| YES | Input Register | 4220 | r_PARS_ReturnPressure.MinimumY1 | 2 | Floating point | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| YES | Input Register | 4222 | r_PARS_ReturnPressure.MinimumY2 | 2 | Floating point | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| YES | Discrete Input | 4201 | r_PARS_ReturnPressure.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 4200 | r_PARS_ReturnPressure.RemoteValueX1 | 2 | Floating point | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA
| YES | Holding Register | 4202 | r_PARS_ReturnPressure.RemoteValueX2 | 2 | Floating point | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA
| YES | Holding Register | 4204 | r_PARS_ReturnPressure.RemoteValueY1 | 2 | Floating point | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi
| YES | Holding Register | 4206 | r_PARS_ReturnPressure.RemoteValueY2 | 2 | Floating point | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi
| NO | Input Register | 4300 | r_PARS_AnalogSetpoint.CurrentValueX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4302 | r_PARS_AnalogSetpoint.CurrentValueX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4304 | r_PARS_AnalogSetpoint.CurrentValueY1 | 2 | Floating point | Not currently implemented. | psi
| NO | Input Register | 4306 | r_PARS_AnalogSetpoint.CurrentValueY2 | 2 | Floating point | Not currently implemented. | psi
| NO | Discrete Input | 4300 | r_PARS_AnalogSetpoint.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 4308 | r_PARS_AnalogSetpoint.MaximumX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4310 | r_PARS_AnalogSetpoint.MaximumX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4312 | r_PARS_AnalogSetpoint.MaximumY1 | 2 | Floating point | Not currently implemented. | psi
| NO | Input Register | 4314 | r_PARS_AnalogSetpoint.MaximumY2 | 2 | Floating point | Not currently implemented. | psi
| NO | Input Register | 4316 | r_PARS_AnalogSetpoint.MinimumX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4318 | r_PARS_AnalogSetpoint.MinimumX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4320 | r_PARS_AnalogSetpoint.MinimumY1 | 2 | Floating point | Not currently implemented. | psi
| NO | Input Register | 4322 | r_PARS_AnalogSetpoint.MinimumY2 | 2 | Floating point | Not currently implemented. | psi
| NO | Discrete Input | 4301 | r_PARS_AnalogSetpoint.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 4300 | r_PARS_AnalogSetpoint.RemoteValueX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Holding Register | 4302 | r_PARS_AnalogSetpoint.RemoteValueX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Holding Register | 4304 | r_PARS_AnalogSetpoint.RemoteValueY1 | 2 | Floating point | Not currently implemented. | psi
| NO | Holding Register | 4306 | r_PARS_AnalogSetpoint.RemoteValueY2 | 2 | Floating point | Not currently implemented. | psi
| YES | Input Register | 4400 | r_PARS_AnalogProcessRetransmit.CurrentValueX1 | 2 | Floating point | Controller-measured temperature that will correspond to the voltage/current given by Y1, in units of degrees Celsius (°C). | °C
| YES | Input Register | 4402 | r_PARS_AnalogProcessRetransmit.CurrentValueX2 | 2 | Floating point | Controller-measured temperature that will correspond to the voltage/current given by Y2, in units of degrees Celsius (°C). | °C
| YES | Input Register | 4404 | r_PARS_AnalogProcessRetransmit.CurrentValueY1 | 2 | Floating point | The voltage/current output that corresponds to the temperature specified by X1, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Input Register | 4406 | r_PARS_AnalogProcessRetransmit.CurrentValueY2 | 2 | Floating point | The voltage/current output that corresponds to the temperature specified by X2, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Discrete Input | 4400 | r_PARS_AnalogProcessRetransmit.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 4408 | r_PARS_AnalogProcessRetransmit.MaximumX1 | 2 | Floating point | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of degrees Celsius (°C). | °C
| YES | Input Register | 4410 | r_PARS_AnalogProcessRetransmit.MaximumX2 | 2 | Floating point | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of degrees Celsius (°C). | °C
| YES | Input Register | 4412 | r_PARS_AnalogProcessRetransmit.MaximumY1 | 2 | Floating point | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Input Register | 4414 | r_PARS_AnalogProcessRetransmit.MaximumY2 | 2 | Floating point | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Input Register | 4416 | r_PARS_AnalogProcessRetransmit.MinimumX1 | 2 | Floating point | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of degrees Celsius (°C). | °C
| YES | Input Register | 4418 | r_PARS_AnalogProcessRetransmit.MinimumX2 | 2 | Floating point | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of degrees Celsius (°C). | °C
| YES | Input Register | 4420 | r_PARS_AnalogProcessRetransmit.MinimumY1 | 2 | Floating point | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Input Register | 4422 | r_PARS_AnalogProcessRetransmit.MinimumY2 | 2 | Floating point | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Discrete Input | 4401 | r_PARS_AnalogProcessRetransmit.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 4400 | r_PARS_AnalogProcessRetransmit.RemoteValueX1 | 2 | Floating point | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of degrees Celsius (°C). | °C
| YES | Holding Register | 4402 | r_PARS_AnalogProcessRetransmit.RemoteValueX2 | 2 | Floating point | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of degrees Celsius (°C). | °C
| YES | Holding Register | 4404 | r_PARS_AnalogProcessRetransmit.RemoteValueY1 | 2 | Floating point | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Holding Register | 4406 | r_PARS_AnalogProcessRetransmit.RemoteValueY2 | 2 | Floating point | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| YES | Input Register | 4500 | r_PARS_AnalogFlowMeter.CurrentValueX1 | 2 | Floating point | Flowmeter-produced voltage/current that will correspond to the flowrate given by Y1, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Input Register | 4502 | r_PARS_AnalogFlowMeter.CurrentValueX2 | 2 | Floating point | Flowmeter-produced voltage/current that will correspond to the flowrate given by Y2, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Input Register | 4504 | r_PARS_AnalogFlowMeter.CurrentValueY1 | 2 | Floating point | Flowrate that will correspond to the voltage/current specified by X1, in units of gallons per minute (gpm). | gpm
| YES | Input Register | 4506 | r_PARS_AnalogFlowMeter.CurrentValueY2 | 2 | Floating point | Flowrate that will correspond to the voltage/current specified by X2, in units of gallons per minute (gpm). | gpm
| YES | Discrete Input | 4500 | r_PARS_AnalogFlowMeter.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 4508 | r_PARS_AnalogFlowMeter.MaximumX1 | 2 | Floating point | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Input Register | 4510 | r_PARS_AnalogFlowMeter.MaximumX2 | 2 | Floating point | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Input Register | 4512 | r_PARS_AnalogFlowMeter.MaximumY1 | 2 | Floating point | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of gallons per minute (gpm). | gpm
| YES | Input Register | 4514 | r_PARS_AnalogFlowMeter.MaximumY2 | 2 | Floating point | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of gallons per minute (gpm). | gpm
| YES | Input Register | 4516 | r_PARS_AnalogFlowMeter.MinimumX1 | 2 | Floating point | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Input Register | 4518 | r_PARS_AnalogFlowMeter.MinimumX2 | 2 | Floating point | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Input Register | 4520 | r_PARS_AnalogFlowMeter.MinimumY1 | 2 | Floating point | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of gallons per minute (gpm). | gpm
| YES | Input Register | 4522 | r_PARS_AnalogFlowMeter.MinimumY2 | 2 | Floating point | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of gallons per minute (gpm). | gpm
| YES | Discrete Input | 4501 | r_PARS_AnalogFlowMeter.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 4500 | r_PARS_AnalogFlowMeter.RemoteValueX1 | 2 | Floating point | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Holding Register | 4502 | r_PARS_AnalogFlowMeter.RemoteValueX2 | 2 | Floating point | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| YES | Holding Register | 4504 | r_PARS_AnalogFlowMeter.RemoteValueY1 | 2 | Floating point | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of gallons per minute (gpm). | gpm
| YES | Holding Register | 4506 | r_PARS_AnalogFlowMeter.RemoteValueY2 | 2 | Floating point | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of gallons per minute (gpm). | gpm
| NO | Input Register | 4600 | r_PARS_AnalogProcessInput.CurrentValueX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4602 | r_PARS_AnalogProcessInput.CurrentValueX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4604 | r_PARS_AnalogProcessInput.CurrentValueY1 | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 4606 | r_PARS_AnalogProcessInput.CurrentValueY2 | 2 | Floating point | Not currently implemented. | °C
| NO | Discrete Input | 4600 | r_PARS_AnalogProcessInput.Implemented | 1 | Bool | Not currently implemented. | Yes/No
| NO | Input Register | 4608 | r_PARS_AnalogProcessInput.MaximumX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4610 | r_PARS_AnalogProcessInput.MaximumX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4612 | r_PARS_AnalogProcessInput.MaximumY1 | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 4614 | r_PARS_AnalogProcessInput.MaximumY2 | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 4616 | r_PARS_AnalogProcessInput.MinimumX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4618 | r_PARS_AnalogProcessInput.MinimumX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Input Register | 4620 | r_PARS_AnalogProcessInput.MinimumY1 | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 4622 | r_PARS_AnalogProcessInput.MinimumY2 | 2 | Floating point | Not currently implemented. | °C
| NO | Discrete Input | 4601 | r_PARS_AnalogProcessInput.RemoteWriteAccess | 1 | Bool | Not currently implemented. | Yes/No
| NO | Holding Register | 4600 | r_PARS_AnalogProcessInput.RemoteValueX1 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Holding Register | 4602 | r_PARS_AnalogProcessInput.RemoteValueX2 | 2 | Floating point | Not currently implemented. | V or mA
| NO | Holding Register | 4604 | r_PARS_AnalogProcessInput.RemoteValueY1 | 2 | Floating point | Not currently implemented. | °C
| NO | Holding Register | 4606 | r_PARS_AnalogProcessInput.RemoteValueY2 | 2 | Floating point | Not currently implemented. | °C
| YES | Input Register | 4700 | r_PARS_RemoteResistorControl.CurrentValueX1 | 2 | Floating point | Controller-measured resistance that will correspond to the controller-interpreted resistance given by Y1, in units of ohms (Ω). | Ω
| YES | Input Register | 4702 | r_PARS_RemoteResistorControl.CurrentValueX2 | 2 | Floating point | Controller-measured resistance that will correspond to the controller-interpreted resistance given by Y2, in units of ohms (Ω). | Ω
| YES | Input Register | 4704 | r_PARS_RemoteResistorControl.CurrentValueY1 | 2 | Floating point | Actual resistance that will correspond to the controller-measured resistance specified by X1, in units of ohms (Ω). | Ω
| YES | Input Register | 4706 | r_PARS_RemoteResistorControl.CurrentValueY2 | 2 | Floating point | Actual resistance that will correspond to the controller-measured resistance specified by X2, in units of ohms (Ω). | Ω
| YES | Discrete Input | 4700 | r_PARS_RemoteResistorControl.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Input Register | 4708 | r_PARS_RemoteResistorControl.MaximumX1 | 2 | Floating point | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of ohms (Ω). | Ω
| YES | Input Register | 4710 | r_PARS_RemoteResistorControl.MaximumX2 | 2 | Floating point | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of ohms (Ω). | Ω
| YES | Input Register | 4712 | r_PARS_RemoteResistorControl.MaximumY1 | 2 | Floating point | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of ohms (Ω). | Ω
| YES | Input Register | 4714 | r_PARS_RemoteResistorControl.MaximumY2 | 2 | Floating point | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of ohms (Ω). | Ω
| YES | Input Register | 4716 | r_PARS_RemoteResistorControl.MinimumX1 | 2 | Floating point | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of ohms (Ω). | Ω
| YES | Input Register | 4718 | r_PARS_RemoteResistorControl.MinimumX2 | 2 | Floating point | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of ohms (Ω). | Ω
| YES | Input Register | 4720 | r_PARS_RemoteResistorControl.MinimumY1 | 2 | Floating point | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of ohms (Ω). | Ω
| YES | Input Register | 4722 | r_PARS_RemoteResistorControl.MinimumY2 | 2 | Floating point | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of ohms (Ω). | Ω
| YES | Discrete Input | 4701 | r_PARS_RemoteResistorControl.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No
| YES | Holding Register | 4700 | r_PARS_RemoteResistorControl.RemoteValueX1 | 2 | Floating point | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω
| YES | Holding Register | 4702 | r_PARS_RemoteResistorControl.RemoteValueX2 | 2 | Floating point | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω
| YES | Holding Register | 4704 | r_PARS_RemoteResistorControl.RemoteValueY1 | 2 | Floating point | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω
| YES | Holding Register | 4706 | r_PARS_RemoteResistorControl.RemoteValueY2 | 2 | Floating point | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω
Networking Parameters, intended for individual read and writing only as necessary.
| YES | Input Register | 5000 | n_PAR_IpAddress.CurrentValue[1] | 1 | Integer | IP address octet #1 for the ethenet network. | N/A
| YES | Input Register | 5001 | n_PAR_IpAddress.CurrentValue[2] | 1 | Integer | IP address octet #2 for the ethenet network. | N/A
| YES | Input Register | 5002 | n_PAR_IpAddress.CurrentValue[3] | 1 | Integer | IP address octet #3 for the ethenet network. | N/A
| YES | Input Register | 5003 | n_PAR_IpAddress.CurrentValue[4] | 1 | Integer | IP address octet #4 for the ethenet network. | N/A
| YES | Discrete Input | 5000 | n_PAR_IpAddress.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 5001 | n_PAR_IpAddress.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | N/A
| YES | Holding Register | 5000 | n_PAR_IpAddress.RemoteValue[1] | 1 | Integer | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5001 | n_PAR_IpAddress.RemoteValue[2] | 1 | Integer | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5002 | n_PAR_IpAddress.RemoteValue[3] | 1 | Integer | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5003 | n_PAR_IpAddress.RemoteValue[4] | 1 | Integer | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Input Register | 5010 | n_PAR_Subnet.CurrentValue[1] | 1 | Integer | Subnet mask octet #1 for the ethenet network. | N/A
| YES | Input Register | 5011 | n_PAR_Subnet.CurrentValue[2] | 1 | Integer | Subnet mask octet #2 for the ethenet network. | N/A
| YES | Input Register | 5012 | n_PAR_Subnet.CurrentValue[3] | 1 | Integer | Subnet mask octet #3 for the ethenet network. | N/A
| YES | Input Register | 5013 | n_PAR_Subnet.CurrentValue[4] | 1 | Integer | Subnet mask octet #4 for the ethenet network. | N/A
| YES | Discrete Input | 5010 | n_PAR_Subnet.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 5011 | n_PAR_Subnet.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | N/A
| YES | Holding Register | 5010 | n_PAR_Subnet.RemoteValue[1] | 1 | Integer | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5011 | n_PAR_Subnet.RemoteValue[2] | 1 | Integer | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5012 | n_PAR_Subnet.RemoteValue[3] | 1 | Integer | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5013 | n_PAR_Subnet.RemoteValue[4] | 1 | Integer | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Input Register | 5020 | n_PAR_Gateway.CurrentValue[1] | 1 | Integer | Gateway octet #1 for the ethenet network. | N/A
| YES | Input Register | 5021 | n_PAR_Gateway.CurrentValue[2] | 1 | Integer | Gateway octet #2 for the ethenet network. | N/A
| YES | Input Register | 5022 | n_PAR_Gateway.CurrentValue[3] | 1 | Integer | Gateway octet #3 for the ethenet network. | N/A
| YES | Input Register | 5023 | n_PAR_Gateway.CurrentValue[4] | 1 | Integer | Gateway octet #4 for the ethenet network. | N/A
| YES | Discrete Input | 5020 | n_PAR_Gateway.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 5021 | n_PAR_Gateway.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | N/A
| YES | Holding Register | 5020 | n_PAR_Gateway.RemoteValue[1] | 1 | Integer | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5021 | n_PAR_Gateway.RemoteValue[2] | 1 | Integer | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5022 | n_PAR_Gateway.RemoteValue[3] | 1 | Integer | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5023 | n_PAR_Gateway.RemoteValue[4] | 1 | Integer | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Input Register | 5030 | n_PAR_DnsAddress1.CurrentValue[1] | 1 | Integer | DNS server #1 IP address octet #1 for the ethenet network. | N/A
| YES | Input Register | 5031 | n_PAR_DnsAddress1.CurrentValue[2] | 1 | Integer | DNS server #1 IP address octet #2 for the ethenet network. | N/A
| YES | Input Register | 5032 | n_PAR_DnsAddress1.CurrentValue[3] | 1 | Integer | DNS server #1 IP address octet #3 for the ethenet network. | N/A
| YES | Input Register | 5033 | n_PAR_DnsAddress1.CurrentValue[4] | 1 | Integer | DNS server #1 IP address octet #4 for the ethenet network. | N/A
| YES | Discrete Input | 5030 | n_PAR_DnsAddress1.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 5031 | n_PAR_DnsAddress1.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | N/A
| YES | Holding Register | 5030 | n_PAR_DnsAddress1.RemoteValue[1] | 1 | Integer | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5031 | n_PAR_DnsAddress1.RemoteValue[2] | 1 | Integer | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5032 | n_PAR_DnsAddress1.RemoteValue[3] | 1 | Integer | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5033 | n_PAR_DnsAddress1.RemoteValue[4] | 1 | Integer | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Input Register | 5040 | n_PAR_DnsAddress2.CurrentValue[1] | 1 | Integer | DNS server #2 IP address octet #1 for the ethenet network. | N/A
| YES | Input Register | 5041 | n_PAR_DnsAddress2.CurrentValue[2] | 1 | Integer | DNS server #2 IP address octet #2 for the ethenet network. | N/A
| YES | Input Register | 5042 | n_PAR_DnsAddress2.CurrentValue[3] | 1 | Integer | DNS server #2 IP address octet #3 for the ethenet network. | N/A
| YES | Input Register | 5043 | n_PAR_DnsAddress2.CurrentValue[4] | 1 | Integer | DNS server #2 IP address octet #4 for the ethenet network. | N/A
| YES | Discrete Input | 5040 | n_PAR_DnsAddress2.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 5041 | n_PAR_DnsAddress2.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | N/A
| YES | Holding Register | 5040 | n_PAR_DnsAddress2.RemoteValue[1] | 1 | Integer | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5041 | n_PAR_DnsAddress2.RemoteValue[2] | 1 | Integer | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5042 | n_PAR_DnsAddress2.RemoteValue[3] | 1 | Integer | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5043 | n_PAR_DnsAddress2.RemoteValue[4] | 1 | Integer | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Input Register | 5050 | n_PAR_NtpAddress.CurrentValue[1] | 1 | Integer | NTP server IP address octet #1 for the ethenet network. | N/A
| YES | Input Register | 5051 | n_PAR_NtpAddress.CurrentValue[2] | 1 | Integer | NTP server IP address octet #2 for the ethenet network. | N/A
| YES | Input Register | 5052 | n_PAR_NtpAddress.CurrentValue[3] | 1 | Integer | NTP server IP address octet #3 for the ethenet network. | N/A
| YES | Input Register | 5053 | n_PAR_NtpAddress.CurrentValue[4] | 1 | Integer | NTP server IP address octet #4 for the ethenet network. | N/A
| YES | Discrete Input | 5050 | n_PAR_NtpAddress.Implemented | 1 | Bool | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| YES | Discrete Input | 5051 | n_PAR_NtpAddress.RemoteWriteAccess | 1 | Bool | Determines if remote values will currently be accepted from .RemoteValue. | N/A
| YES | Holding Register | 5050 | n_PAR_NtpAddress.RemoteValue[1] | 1 | Integer | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5051 | n_PAR_NtpAddress.RemoteValue[2] | 1 | Integer | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5052 | n_PAR_NtpAddress.RemoteValue[3] | 1 | Integer | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A
| YES | Holding Register | 5053 | n_PAR_NtpAddress.RemoteValue[4] | 1 | Integer | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A
Warnings, intended for individual read only as necessary.
| YES | Discrete Input | 6000 | b_WRN_PumpOverload.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. The pump overload protector has tripped from too much pump motor current. This is typically caused by excessive flow in the process loop. Check the fluid loop for too much flow or restrict it. Manually reset overload protector in electrical panel. | Inactive/Active
| YES | Discrete Input | 6001 | b_WRN_PumpOverload.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6002 | b_WRN_PumpOverload.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6000 | b_WRN_PumpOverload.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6010 | b_WRN_FlowmeterLowFlow.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. There is insufficient flow in the process loop for an extended period of time. | Inactive/Active
| YES | Discrete Input | 6011 | b_WRN_FlowmeterLowFlow.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6012 | b_WRN_FlowmeterLowFlow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6010 | b_WRN_FlowmeterLowFlow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| NO | Discrete Input | 6020 | b_WRN_FO_SupToRet_SupRTD_Open.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6021 | b_WRN_FO_SupToRet_SupRTD_Open.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6022 | b_WRN_FO_SupToRet_SupRTD_Open.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6020 | b_WRN_FO_SupToRet_SupRTD_Open.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6030 | b_WRN_FO_SupToRet_SupRTD_Shorted.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6031 | b_WRN_FO_SupToRet_SupRTD_Shorted.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6032 | b_WRN_FO_SupToRet_SupRTD_Shorted.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6030 | b_WRN_FO_SupToRet_SupRTD_Shorted.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6040 | b_WRN_FO_SupToRet_SupRTD_Other.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6041 | b_WRN_FO_SupToRet_SupRTD_Other.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6042 | b_WRN_FO_SupToRet_SupRTD_Other.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6040 | b_WRN_FO_SupToRet_SupRTD_Other.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6050 | b_WRN_FO_RetToSup_RetRTD_Open.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6051 | b_WRN_FO_RetToSup_RetRTD_Open.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6052 | b_WRN_FO_RetToSup_RetRTD_Open.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6050 | b_WRN_FO_RetToSup_RetRTD_Open.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6060 | b_WRN_FO_RetToSup_RetRTD_Shorted.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6061 | b_WRN_FO_RetToSup_RetRTD_Shorted.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6062 | b_WRN_FO_RetToSup_RetRTD_Shorted.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6060 | b_WRN_FO_RetToSup_RetRTD_Shorted.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6070 | b_WRN_FO_RetToSup_RetRTD_Other.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6071 | b_WRN_FO_RetToSup_RetRTD_Other.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6072 | b_WRN_FO_RetToSup_RetRTD_Other.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6070 | b_WRN_FO_RetToSup_RetRTD_Other.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6080 | b_WRN_FO_RemToRet_RemRTD_Open.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6081 | b_WRN_FO_RemToRet_RemRTD_Open.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6082 | b_WRN_FO_RemToRet_RemRTD_Open.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6080 | b_WRN_FO_RemToRet_RemRTD_Open.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6090 | b_WRN_FO_RemToRet_RemRTD_Shorted.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6091 | b_WRN_FO_RemToRet_RemRTD_Shorted.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6092 | b_WRN_FO_RemToRet_RemRTD_Shorted.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6090 | b_WRN_FO_RemToRet_RemRTD_Shorted.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6100 | b_WRN_FO_RemToRet_RemRTD_Other.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6101 | b_WRN_FO_RemToRet_RemRTD_Other.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6102 | b_WRN_FO_RemToRet_RemRTD_Other.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6100 | b_WRN_FO_RemToRet_RemRTD_Other.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6110 | b_WRN_FO_AnaToRet_AnaProcInHigh.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6111 | b_WRN_FO_AnaToRet_AnaProcInHigh.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6112 | b_WRN_FO_AnaToRet_AnaProcInHigh.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6110 | b_WRN_FO_AnaToRet_AnaProcInHigh.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6120 | b_WRN_FO_AnaToRet_AnaProcInLow.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6121 | b_WRN_FO_AnaToRet_AnaProcInLow.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6122 | b_WRN_FO_AnaToRet_AnaProcInLow.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6120 | b_WRN_FO_AnaToRet_AnaProcInLow.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6130 | b_WRN_FO_AnaToRet_AnaProcInOther.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6131 | b_WRN_FO_AnaToRet_AnaProcInOther.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6132 | b_WRN_FO_AnaToRet_AnaProcInOther.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6130 | b_WRN_FO_AnaToRet_AnaProcInOther.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6140 | b_WRN_FO_NetToRet_NetProcHigh.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6141 | b_WRN_FO_NetToRet_NetProcHigh.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6142 | b_WRN_FO_NetToRet_NetProcHigh.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6140 | b_WRN_FO_NetToRet_NetProcHigh.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6150 | b_WRN_FO_NetToRet_NetProcLow.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6151 | b_WRN_FO_NetToRet_NetProcLow.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6152 | b_WRN_FO_NetToRet_NetProcLow.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6150 | b_WRN_FO_NetToRet_NetProcLow.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6160 | b_WRN_FO_NetToRet_NetProcHB.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6161 | b_WRN_FO_NetToRet_NetProcHB.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6162 | b_WRN_FO_NetToRet_NetProcHB.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6160 | b_WRN_FO_NetToRet_NetProcHB.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6170 | b_WRN_FO_AnaToMain_AnaSP_High.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6171 | b_WRN_FO_AnaToMain_AnaSP_High.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6172 | b_WRN_FO_AnaToMain_AnaSP_High.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6170 | b_WRN_FO_AnaToMain_AnaSP_High.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6180 | b_WRN_FO_AnaToMain_AnaSP_Low.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6181 | b_WRN_FO_AnaToMain_AnaSP_Low.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6182 | b_WRN_FO_AnaToMain_AnaSP_Low.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6180 | b_WRN_FO_AnaToMain_AnaSP_Low.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6190 | b_WRN_FO_AnaToMain_AnaSP_Other.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6191 | b_WRN_FO_AnaToMain_AnaSP_Other.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6192 | b_WRN_FO_AnaToMain_AnaSP_Other.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6190 | b_WRN_FO_AnaToMain_AnaSP_Other.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6200 | b_WRN_FO_NetToMain_NetSP_High.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6201 | b_WRN_FO_NetToMain_NetSP_High.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6202 | b_WRN_FO_NetToMain_NetSP_High.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6200 | b_WRN_FO_NetToMain_NetSP_High.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6210 | b_WRN_FO_NetToMain_NetSP_Low.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6211 | b_WRN_FO_NetToMain_NetSP_Low.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6212 | b_WRN_FO_NetToMain_NetSP_Low.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6210 | b_WRN_FO_NetToMain_NetSP_Low.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 6220 | b_WRN_FO_NetToMain_NetSP_HB.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 6221 | b_WRN_FO_NetToMain_NetSP_HB.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 6222 | b_WRN_FO_NetToMain_NetSP_HB.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 6220 | b_WRN_FO_NetToMain_NetSP_HB.Count | 2 | Integer | Not currently enabled. | Events
| YES | Discrete Input | 6230 | b_WRN_PressureBelowMinimum.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. Process fluid pressurization supply is too low or there is a leak in the process loop. Machine will automatically restart when pressure returns. | Inactive/Active
| YES | Discrete Input | 6231 | b_WRN_PressureBelowMinimum.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6232 | b_WRN_PressureBelowMinimum.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6230 | b_WRN_PressureBelowMinimum.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6240 | b_WRN_PressureNotHighEnough.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. Process loop pressure is too low for the actual high system temperature. The process loop is pressurized by the incoming cooling water, and must remain sufficient, especially at high operating temperatures. Increase the cooling water supply pressure. Operate the system at a lower temperature setpoint. | Inactive/Active
| YES | Discrete Input | 6241 | b_WRN_PressureNotHighEnough.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6242 | b_WRN_PressureNotHighEnough.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6240 | b_WRN_PressureNotHighEnough.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6250 | b_WRN_SetpointTooHighForPressure.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. Setpoint is too high for current system pressure. Operate the system at a lower temperature setpoint. Increase the cooling water supply pressure. | Inactive/Active
| YES | Discrete Input | 6251 | b_WRN_SetpointTooHighForPressure.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6252 | b_WRN_SetpointTooHighForPressure.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6250 | b_WRN_SetpointTooHighForPressure.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6260 | b_WRN_SupplyRTD_Open.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. An OPEN CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "To Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "To process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 6261 | b_WRN_SupplyRTD_Open.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6262 | b_WRN_SupplyRTD_Open.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6260 | b_WRN_SupplyRTD_Open.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6270 | b_WRN_SupplyRTD_Shorted.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A SHORT CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "To Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "To process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 6271 | b_WRN_SupplyRTD_Shorted.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6272 | b_WRN_SupplyRTD_Shorted.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6270 | b_WRN_SupplyRTD_Shorted.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6280 | b_WRN_SupplyRTD_Other.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A CHANNEL FAULT has occurred in the "To Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit. | Inactive/Active
| YES | Discrete Input | 6281 | b_WRN_SupplyRTD_Other.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6282 | b_WRN_SupplyRTD_Other.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6280 | b_WRN_SupplyRTD_Other.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6290 | b_WRN_ReturnRTD_Open.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. An OPEN CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "From Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "From process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 6291 | b_WRN_ReturnRTD_Open.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6292 | b_WRN_ReturnRTD_Open.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6290 | b_WRN_ReturnRTD_Open.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6300 | b_WRN_ReturnRTD_Shorted.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A SHORT CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "From Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "From process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 6301 | b_WRN_ReturnRTD_Shorted.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6302 | b_WRN_ReturnRTD_Shorted.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6300 | b_WRN_ReturnRTD_Shorted.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6310 | b_WRN_ReturnRTD_Other.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A CHANNEL FAULT has occurred in the "From Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit. | Inactive/Active
| YES | Discrete Input | 6311 | b_WRN_ReturnRTD_Other.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6312 | b_WRN_ReturnRTD_Other.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6310 | b_WRN_ReturnRTD_Other.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6320 | b_WRN_SupplyTransducerHigh.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. The machine can continue to operate, but will be unable to approximate flow. Check the "To Process" pressure transducer. Check the analog wiring. | Inactive/Active
| YES | Discrete Input | 6321 | b_WRN_SupplyTransducerHigh.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6322 | b_WRN_SupplyTransducerHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6320 | b_WRN_SupplyTransducerHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6330 | b_WRN_SupplyTransducerLow.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. The machine can continue to operate, but will be unable to approximate flow. Check the "To Process" pressure transducer. Check the analog wiring. | Inactive/Active
| YES | Discrete Input | 6331 | b_WRN_SupplyTransducerLow.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6332 | b_WRN_SupplyTransducerLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6330 | b_WRN_SupplyTransducerLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6340 | b_WRN_SupplyTransducerOther.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A CHANNEL FAULT has occurred on the "To Process" pressure transducer or wiring. The machine can continue to operate, but will be unable to approximate flow. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit. | Inactive/Active
| YES | Discrete Input | 6341 | b_WRN_SupplyTransducerOther.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6342 | b_WRN_SupplyTransducerOther.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6340 | b_WRN_SupplyTransducerOther.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6350 | b_WRN_AnaFlowmeterHigh.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. The machine can continue to operate, but will be unable to measure flow or take action on low flow conditions. Check the flowmeter. Check the analog wiring. | Inactive/Active
| YES | Discrete Input | 6351 | b_WRN_AnaFlowmeterHigh.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6352 | b_WRN_AnaFlowmeterHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6350 | b_WRN_AnaFlowmeterHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6360 | b_WRN_AnaFlowmeterLow.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. The machine can continue to operate, but will be unable to measure flow or take action on low flow conditions. Check the flowmeter. Check the analog wiring. | Inactive/Active
| YES | Discrete Input | 6361 | b_WRN_AnaFlowmeterLow.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6362 | b_WRN_AnaFlowmeterLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6360 | b_WRN_AnaFlowmeterLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6370 | b_WRN_AnaFlowmeterOther.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A CHANNEL FAULT has occurred on the FLOWMETER or wiring. The machine can continue to operate, but will be unable to measure flow or take action on low flow conditions. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit. | Inactive/Active
| YES | Discrete Input | 6371 | b_WRN_AnaFlowmeterOther.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6372 | b_WRN_AnaFlowmeterOther.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6370 | b_WRN_AnaFlowmeterOther.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6380 | b_WRN_FlashMemoryWrites.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. Flash memory writes are excessive. Contact the Service department of the manufacturer. | Inactive/Active
| YES | Discrete Input | 6381 | b_WRN_FlashMemoryWrites.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6382 | b_WRN_FlashMemoryWrites.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6380 | b_WRN_FlashMemoryWrites.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6390 | b_WRN_HighDeviation.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. The temperature has deviated too high for too long above the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/blocked cooling valve. Check for a failed (stuck on) heater contactor. | Inactive/Active
| YES | Discrete Input | 6391 | b_WRN_HighDeviation.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6392 | b_WRN_HighDeviation.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6390 | b_WRN_HighDeviation.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6400 | b_WRN_LowDeviation.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. The temperature has deviated too low for too long below the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/stuck open cooling valve. Check for a failed heater contactor. | Inactive/Active
| YES | Discrete Input | 6401 | b_WRN_LowDeviation.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6402 | b_WRN_LowDeviation.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6400 | b_WRN_LowDeviation.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6410 | b_WRN_NetworkHeartbeatLost.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. The NETWORK HEARTBEAT HAS BEEN LOST after having been initially established. Fix network or remote node. Change Network Timeout action or timeout period. | Inactive/Active
| YES | Discrete Input | 6411 | b_WRN_NetworkHeartbeatLost.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6412 | b_WRN_NetworkHeartbeatLost.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6410 | b_WRN_NetworkHeartbeatLost.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6420 | b_WRN_RemoteSlaveWarningActive.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. A warning has been inherrited from banked Slave unit. Rectify the warning on the banked slave unit. Change the master to not register banked slave warnings. | Inactive/Active
| YES | Discrete Input | 6421 | b_WRN_RemoteSlaveWarningActive.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6422 | b_WRN_RemoteSlaveWarningActive.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6420 | b_WRN_RemoteSlaveWarningActive.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6430 | b_WRN_TooManyHeaterCycles.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. The machine is being used in a manner that cycles the heaters too frequently. This will wear out the heater contactor prematurely, leading to early machine failure. The PID should be re-tuned. SSR-equipped model should be used for this application. | Inactive/Active
| YES | Discrete Input | 6431 | b_WRN_TooManyHeaterCycles.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6432 | b_WRN_TooManyHeaterCycles.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6430 | b_WRN_TooManyHeaterCycles.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6440 | b_WRN_WornOutHeaterContactor.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. The HEATER CONTACTOR is nearing the end of its operational life. Please replace the component whenever possible to eliminate this source of eventual failure. Replace the electromechanical heater contactor. | Inactive/Active
| YES | Discrete Input | 6441 | b_WRN_WornOutHeaterContactor.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6442 | b_WRN_WornOutHeaterContactor.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6440 | b_WRN_WornOutHeaterContactor.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 6450 | b_WRN_ClockNotSet.Value | 1 | Bool | This bit signifies whether or not this warning is currently active. The DATE and TIME have not been set in the controller. Trends, schedules, warnings and alarms may not operate properly until this is completed. Set the DATE and TIME. | Inactive/Active
| YES | Discrete Input | 6451 | b_WRN_ClockNotSet.Enable | 1 | Bool | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| YES | Discrete Input | 6452 | b_WRN_ClockNotSet.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 6450 | b_WRN_ClockNotSet.Count | 2 | Integer | Number of times .Value has been triggered. | Events
Alarms, intended for individual read only as necessary.
| YES | Discrete Input | 7000 | b_ALM_IO_HMI_ConnectionFailure.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The touchscreen controller has lost connection with all of the IO modules. The touchscreen and IO modules are interconnected via 2 conductors (plus shield). They are each supplied with 24VDC separately. All must be present for the system to function properly. See electrical prints for details. Verify connections at touchscreen and first IO module. Check all IO modules are powered-up/illuminated. | Inactive/Active
| YES | Discrete Input | 7001 | b_ALM_IO_HMI_ConnectionFailure.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7002 | b_ALM_IO_HMI_ConnectionFailure.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7000 | b_ALM_IO_HMI_ConnectionFailure.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7010 | b_ALM_IO_ModuleLinkFailure.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A particular IO module and all IO modules to its right have suffered a communication failure with the touchscreen. Connection on the left side of an IO module is likely bad. Check that IO modules are tightly mated to each other. Check IO modules are seated & locked on DIN rail. | Inactive/Active
| YES | Discrete Input | 7011 | b_ALM_IO_ModuleLinkFailure.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7012 | b_ALM_IO_ModuleLinkFailure.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7010 | b_ALM_IO_ModuleLinkFailure.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7020 | b_ALM_IO_HardwareMismatch.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. An IO module is not the correct part number. Replace the IO module with the correct component. Check for accidental mixed-up order of IO modules. | Inactive/Active
| YES | Discrete Input | 7021 | b_ALM_IO_HardwareMismatch.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7022 | b_ALM_IO_HardwareMismatch.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7020 | b_ALM_IO_HardwareMismatch.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7030 | b_ALM_IO_ModuleInternalFailure.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. IO module has an internal failure. IO modules are numbered from left to right, starting with #1 ("X20BR7300") at the leftmost position. Replace the faulty IO module. Inspect machine for root cause of IO module failure. | Inactive/Active
| YES | Discrete Input | 7031 | b_ALM_IO_ModuleInternalFailure.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7032 | b_ALM_IO_ModuleInternalFailure.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7030 | b_ALM_IO_ModuleInternalFailure.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7040 | b_ALM_IO_PointFailure.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. An IO module has an internal failure. Replace the faulty IO module. Inspect machine for root cause of IO module failure. | Inactive/Active
| YES | Discrete Input | 7041 | b_ALM_IO_PointFailure.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7042 | b_ALM_IO_PointFailure.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7040 | b_ALM_IO_PointFailure.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7050 | b_ALM_PowerSupplyLow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The 24VDC power supply voltage going to the IO modules is low. This 24VDC power is connected to terminals 15 (+) and 16 (-) of module #1 ("X20BR7300"). Check for voltage and wiring integrity. | Inactive/Active
| YES | Discrete Input | 7051 | b_ALM_PowerSupplyLow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7052 | b_ALM_PowerSupplyLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7050 | b_ALM_PowerSupplyLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7060 | b_ALM_LogicSupplyLow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The logic power supply for the IO modules is low. The logic supply is generated by the leftmost module #1 ("X20BR7300"). Check connections between all IO modules & 24VDC. Replace module #1 ("X20BR7300"). | Inactive/Active
| YES | Discrete Input | 7061 | b_ALM_LogicSupplyLow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7062 | b_ALM_LogicSupplyLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7060 | b_ALM_LogicSupplyLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7070 | b_ALM_Overtemperature.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. DISCONNECT POWER TO THE MACHINE! A hardware overtemperature condition has been detected by a missing digital input which is normally energized. This input is typically jumpered to +24VDC, but may be connected through internal optional components (SSRs) or external components at the installation. Check for missing jumper or external equipment. Check for failed cooling fan / blocked airflow on SSRs. | Inactive/Active
| YES | Discrete Input | 7071 | b_ALM_Overtemperature.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7072 | b_ALM_Overtemperature.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7070 | b_ALM_Overtemperature.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7080 | b_ALM_HeaterContactorStuckClosed.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. DISCONNECT POWER TO THE MACHINE! The heater contactor has been detected as stuck closed (energized). Cooling water is being introduced and circulated intentionally to cool the heater. The heater contactor has likely welded closed due to overuse or end-of-life. Replace the faulty heater contactor. Check wiring on heater contactor coil & aux contacts. | Inactive/Active
| YES | Discrete Input | 7081 | b_ALM_HeaterContactorStuckClosed.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7082 | b_ALM_HeaterContactorStuckClosed.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7080 | b_ALM_HeaterContactorStuckClosed.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7090 | b_ALM_FactoryTempHigh.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. DISCONNECT POWER TO THE MACHINE! The process loop has exceeded the maximum permitted temperature. Cooling water is being introduced and circulated intentionally to cool the loop. This could be caused by an internal malfunction or oversized external heat source. Replace faulty cooling valve or cooling water supply. Replace faulty heater contactor. | Inactive/Active
| YES | Discrete Input | 7091 | b_ALM_FactoryTempHigh.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7092 | b_ALM_FactoryTempHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7090 | b_ALM_FactoryTempHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7100 | b_ALM_Unbranded.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. No branding nor model has been specified. Set these in "Machine Configuration" within the "Configuration" menu. Select a brand and model for this machine. | Inactive/Active
| YES | Discrete Input | 7101 | b_ALM_Unbranded.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7102 | b_ALM_Unbranded.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7100 | b_ALM_Unbranded.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7111 | b_ALM_OptionsNotSet.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The mechanical configuration and factory-installed options have not yet been set. Set these in "Machine Configuration" within the "Configuration" menu. Set the mechanical configuration (pump, heater, etc). Set options (pressure transducers, mold purge, etc). | Inactive/Active
| YES | Discrete Input | 7112 | b_ALM_OptionsNotSet.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7113 | b_ALM_OptionsNotSet.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7111 | b_ALM_OptionsNotSet.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7121 | b_ALM_PhaseMonitor.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. There is a problem with the incoming 3-phase electrical power. This is likely due to reverse phase rotation, a missing phase, or a low leg. For reverse phase rotation, swap any two phases on the incoming power. (This is hazardous work and must be performed by a qualitied electrician). Correct reverse phase rotation or missing phase. Replace blown pump fuse (if equipped). | Inactive/Active
| YES | Discrete Input | 7122 | b_ALM_PhaseMonitor.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7123 | b_ALM_PhaseMonitor.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7121 | b_ALM_PhaseMonitor.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7131 | b_ALM_PumpContactorStuckClosed.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. DISCONNECT POWER TO THE MACHINE! The pump contactor has been detected as stuck closed (energized). The pump contactor has likely welded closed due to overuse or end-of-life. Replace the faulty pump contactor. Check wiring on pump contactor coil & aux contacts. | Inactive/Active
| YES | Discrete Input | 7132 | b_ALM_PumpContactorStuckClosed.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7133 | b_ALM_PumpContactorStuckClosed.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7131 | b_ALM_PumpContactorStuckClosed.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7141 | b_ALM_HeaterContactorStuckOpen.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The heater contactor has been detected as stuck open (deenergized). The heater contactor likely has a faulty/open coil circuit, or there is mechanical binding on its internal armature which is preventing movement. Replace the faulty heater contactor. Check wiring on heater contactor coil & aux contacts. | Inactive/Active
| YES | Discrete Input | 7142 | b_ALM_HeaterContactorStuckOpen.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7143 | b_ALM_HeaterContactorStuckOpen.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7141 | b_ALM_HeaterContactorStuckOpen.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7151 | b_ALM_PumpContactorStuckOpen.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The pump contactor has been detected as stuck open (deenergized). The pump contactor likely has a faulty/open coil circuit, or there is mechanical binding on its internal armature which is preventing movement. Replace the faulty pump contactor. Check wiring on pump contactor coil & aux contacts. | Inactive/Active
| YES | Discrete Input | 7152 | b_ALM_PumpContactorStuckOpen.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7153 | b_ALM_PumpContactorStuckOpen.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7151 | b_ALM_PumpContactorStuckOpen.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7161 | b_ALM_PressureTooHigh.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. Excessive pressure has been detected in the process loop. The source of this pressure is likely from the cooling water supply. This condition can also be caused by a check valve installed on the cooling water inlet without pressure transducers to automatically relieve thermally-induced pressure. Reduce cooling water pressure. Check for stuck closed cooling valve. | Inactive/Active
| YES | Discrete Input | 7162 | b_ALM_PressureTooHigh.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7163 | b_ALM_PressureTooHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7161 | b_ALM_PressureTooHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7171 | b_ALM_ElecPanelTooHot.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. Excessive temperature has been detected in the electrical panel. This will lead to component failure or erratic operation. The temperature is sensed within the touchscreen controller. Replace the failed electrical panel cooling fan. Check for hot ambient or blocked intake/exhaust vents. | Inactive/Active
| YES | Discrete Input | 7172 | b_ALM_ElecPanelTooHot.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7173 | b_ALM_ElecPanelTooHot.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7171 | b_ALM_ElecPanelTooHot.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7181 | b_ALM_FactoryTempLow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The process loop has dropped below the minimum permitted temperature. This could be caused by a low ambient temperature, excessive cooling, or oversized external cooling load. In rare cases, it could also be caused by a malfunctioning RTD temperature sensor. Check for excessively low ambient or large cooling load. Repair stuck-open cooling valve and/or faulty heater. | Inactive/Active
| YES | Discrete Input | 7182 | b_ALM_FactoryTempLow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7183 | b_ALM_FactoryTempLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7181 | b_ALM_FactoryTempLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7191 | b_ALM_Brownout.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The machine lost incoming power while it was in operation. This alarm was triggered because the machine was configured to do so. To change this behavior, adjust the "Brownout Monitor" settings in "Setup" within the "Configuration" menu. Establish reliable electric power while in operation. Disable fault in "Machine Configuration" if undesired. | Inactive/Active
| YES | Discrete Input | 7192 | b_ALM_Brownout.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7193 | b_ALM_Brownout.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7191 | b_ALM_Brownout.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7201 | b_ALM_UserTempHigh.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The process loop has exceeded the maximum limit alarm as configured by the operator. This could be caused by loss of cooling water or excessive external heat load. It could also be an incorrectly configured limit alarm. Check for loss of cooling water or faulty cooling valve. Revise the alarm setting to be more appropriate. | Inactive/Active
| YES | Discrete Input | 7202 | b_ALM_UserTempHigh.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7203 | b_ALM_UserTempHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7201 | b_ALM_UserTempHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7211 | b_ALM_UserTempLow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The process loop has dropped below the minimum limit alarm as configured by the operator. This could be caused by excessive cooling water or excessive external cooling load. It could also be an incorrectly configured limit alarm. Check for malfunctioning heater or excessive cool load. Revise the alarm setting to be more appropriate. | Inactive/Active
| YES | Discrete Input | 7212 | b_ALM_UserTempLow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7213 | b_ALM_UserTempLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7211 | b_ALM_UserTempLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7221 | b_ALM_PressureBelowMinimum.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. Process fluid pressurization supply is too low or there is a leak in the process loop. The machine has been configured to NOT restart automatically if low pressure. To change this, select different actions for "Adaptive Max Setpoint" in "Setup" within the "Configuration" menu. | Inactive/Active
| YES | Discrete Input | 7222 | b_ALM_PressureBelowMinimum.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7223 | b_ALM_PressureBelowMinimum.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7221 | b_ALM_PressureBelowMinimum.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7231 | b_ALM_PressureNotHighEnough.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. Process loop pressure is too low for the actual high system temperature. The process loop is pressurized by the incoming cooling water, and must remain sufficient, especially at high operating temperatures. Increase the cooling water supply pressure. Operate the system at a lower temperature setpoint. | Inactive/Active
| YES | Discrete Input | 7232 | b_ALM_PressureNotHighEnough.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7233 | b_ALM_PressureNotHighEnough.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7231 | b_ALM_PressureNotHighEnough.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7241 | b_ALM_LowPressureStandbyTimeout.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. Low pressure has been present at the "From Process" port for an excessive amount of time, causing the machine to stop and not execute an automatic restart. There is likely a fault in the external plumbing, such as low pressure or a closed valve. | Inactive/Active
| YES | Discrete Input | 7242 | b_ALM_LowPressureStandbyTimeout.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7243 | b_ALM_LowPressureStandbyTimeout.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7241 | b_ALM_LowPressureStandbyTimeout.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7251 | b_ALM_LowPressureStrikeout.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. There have been to many low pressure events within a short amount of time. The cooling water plumbing to the equipment is likely too small and is unable to maintain sufficient pressure during operations, or other equipment is consuming too much flow simultaneously. The plumbing to the machine is likely insufficient. Check city/tower/pressure supply or for a leak. | Inactive/Active
| YES | Discrete Input | 7252 | b_ALM_LowPressureStrikeout.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7253 | b_ALM_LowPressureStrikeout.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7251 | b_ALM_LowPressureStrikeout.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7261 | b_ALM_PumpOverload.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The pump overload protector has tripped from too much pump motor current. This is typically caused by excessive flow in the process loop. Check the fluid loop for too much flow or restrict it. Manually reset overload protector in electrical panel. | Inactive/Active
| YES | Discrete Input | 7262 | b_ALM_PumpOverload.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7263 | b_ALM_PumpOverload.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7261 | b_ALM_PumpOverload.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7271 | b_ALM_FlowmeterLowFlow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. There is insufficient flow in the process loop for an extended period of time. | Inactive/Active
| YES | Discrete Input | 7272 | b_ALM_FlowmeterLowFlow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7273 | b_ALM_FlowmeterLowFlow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7271 | b_ALM_FlowmeterLowFlow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7281 | b_ALM_SupplyRTD_Open.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. An OPEN CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the "To Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "To process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 7282 | b_ALM_SupplyRTD_Open.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7283 | b_ALM_SupplyRTD_Open.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7281 | b_ALM_SupplyRTD_Open.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7291 | b_ALM_SupplyRTD_Shorted.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A SHORT CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check "To Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "To process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 7292 | b_ALM_SupplyRTD_Shorted.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7293 | b_ALM_SupplyRTD_Shorted.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7291 | b_ALM_SupplyRTD_Shorted.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7301 | b_ALM_SupplyRTD_Other.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A CHANNEL FAULT has occurred in the "To Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit. | Inactive/Active
| YES | Discrete Input | 7302 | b_ALM_SupplyRTD_Other.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7303 | b_ALM_SupplyRTD_Other.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7301 | b_ALM_SupplyRTD_Other.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7311 | b_ALM_ReturnRTD_Open.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. An OPEN CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check "From Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "From process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 7312 | b_ALM_ReturnRTD_Open.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7313 | b_ALM_ReturnRTD_Open.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7311 | b_ALM_ReturnRTD_Open.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7321 | b_ALM_ReturnRTD_Shorted.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A SHORT CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check "From Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "From process" RTD circuit. | Inactive/Active
| YES | Discrete Input | 7322 | b_ALM_ReturnRTD_Shorted.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7323 | b_ALM_ReturnRTD_Shorted.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7321 | b_ALM_ReturnRTD_Shorted.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7331 | b_ALM_ReturnRTD_Other.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A CHANNEL FAULT has occurred in the "From Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit. | Inactive/Active
| YES | Discrete Input | 7332 | b_ALM_ReturnRTD_Other.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7333 | b_ALM_ReturnRTD_Other.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7331 | b_ALM_ReturnRTD_Other.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7341 | b_ALM_RemoteRTD_Open.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. An OPEN CIRCUIT has occurred in the "Remote" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the "Remote" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "Remote" RTD circuit. | Inactive/Active
| YES | Discrete Input | 7342 | b_ALM_RemoteRTD_Open.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7343 | b_ALM_RemoteRTD_Open.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7341 | b_ALM_RemoteRTD_Open.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7351 | b_ALM_RemoteRTD_Shorted.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A SHORT CIRCUIT has occurred in the "Remote" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the "Remote" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "Remote" RTD circuit. | Inactive/Active
| YES | Discrete Input | 7352 | b_ALM_RemoteRTD_Shorted.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7353 | b_ALM_RemoteRTD_Shorted.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7351 | b_ALM_RemoteRTD_Shorted.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7361 | b_ALM_RemoteRTD_Other.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A CHANNEL FAULT has occurred in the "Remote" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit. | Inactive/Active
| YES | Discrete Input | 7362 | b_ALM_RemoteRTD_Other.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7363 | b_ALM_RemoteRTD_Other.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7361 | b_ALM_RemoteRTD_Other.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7371 | b_ALM_ReturnTransducerHigh.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "From Process" pressure transducer or wiring. This sensor is required for machine operation. Check the "From Process" pressure transducer. Check the analog transducer wiring. | Inactive/Active
| YES | Discrete Input | 7372 | b_ALM_ReturnTransducerHigh.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7373 | b_ALM_ReturnTransducerHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7371 | b_ALM_ReturnTransducerHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7381 | b_ALM_ReturnTransducerLow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "From Process" pressure transducer or wiring. This sensor is required for machine operation. Check the "From Process" pressure transducer. Check the analog transducer wiring. | Inactive/Active
| YES | Discrete Input | 7382 | b_ALM_ReturnTransducerLow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7383 | b_ALM_ReturnTransducerLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7381 | b_ALM_ReturnTransducerLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7391 | b_ALM_ReturnTransducerOther.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A CHANNEL FAULT has occurred on the "From Process" pressure transducer or wiring. This sensor is required for machine operation. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit. | Inactive/Active
| YES | Discrete Input | 7392 | b_ALM_ReturnTransducerOther.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7393 | b_ALM_ReturnTransducerOther.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7391 | b_ALM_ReturnTransducerOther.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7401 | b_ALM_SupplyTransducerHigh.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. Check the "To Process" pressure transducer. Check the analog transducer wiring. | Inactive/Active
| YES | Discrete Input | 7402 | b_ALM_SupplyTransducerHigh.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7403 | b_ALM_SupplyTransducerHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7401 | b_ALM_SupplyTransducerHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7411 | b_ALM_SupplyTransducerLow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. Check the "To Process" pressure transducer. Check the analog transducer wiring. | Inactive/Active
| YES | Discrete Input | 7412 | b_ALM_SupplyTransducerLow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7413 | b_ALM_SupplyTransducerLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7411 | b_ALM_SupplyTransducerLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7421 | b_ALM_SupplyTransducerOther.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A CHANNEL FAULT has occurred on the "To Process" pressure transducer or wiring. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit. | Inactive/Active
| YES | Discrete Input | 7422 | b_ALM_SupplyTransducerOther.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7423 | b_ALM_SupplyTransducerOther.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7421 | b_ALM_SupplyTransducerOther.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| NO | Discrete Input | 7431 | b_ALM_AnaProcInHigh.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7432 | b_ALM_AnaProcInHigh.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7433 | b_ALM_AnaProcInHigh.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7431 | b_ALM_AnaProcInHigh.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7441 | b_ALM_AnaProcInLow.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7442 | b_ALM_AnaProcInLow.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7443 | b_ALM_AnaProcInLow.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7441 | b_ALM_AnaProcInLow.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7451 | b_ALM_AnaProcInOther.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7452 | b_ALM_AnaProcInOther.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7453 | b_ALM_AnaProcInOther.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7451 | b_ALM_AnaProcInOther.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7461 | b_ALM_NetProcHigh.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7462 | b_ALM_NetProcHigh.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7463 | b_ALM_NetProcHigh.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7461 | b_ALM_NetProcHigh.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7471 | b_ALM_NetProcLow.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7472 | b_ALM_NetProcLow.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7473 | b_ALM_NetProcLow.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7471 | b_ALM_NetProcLow.Count | 2 | Integer | Not currently enabled. | Events
| YES | Discrete Input | 7481 | b_ALM_NetProcHeartbeat.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The NETWORK HEARTBEAT HAS BEEN LOST. Heartbeat is necessary because the PROCESS TEMPERATURE is received from the network. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the network integrity. Check network settings in originating network node. | Inactive/Active
| YES | Discrete Input | 7482 | b_ALM_NetProcHeartbeat.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7483 | b_ALM_NetProcHeartbeat.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7481 | b_ALM_NetProcHeartbeat.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| NO | Discrete Input | 7491 | b_ALM_AnaSP_High.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7492 | b_ALM_AnaSP_High.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7493 | b_ALM_AnaSP_High.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7491 | b_ALM_AnaSP_High.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7501 | b_ALM_AnaSP_Low.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7502 | b_ALM_AnaSP_Low.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7503 | b_ALM_AnaSP_Low.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7501 | b_ALM_AnaSP_Low.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7511 | b_ALM_AnaSP_Other.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7512 | b_ALM_AnaSP_Other.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7513 | b_ALM_AnaSP_Other.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7511 | b_ALM_AnaSP_Other.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7521 | b_ALM_NetSP_High.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7522 | b_ALM_NetSP_High.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7523 | b_ALM_NetSP_High.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7521 | b_ALM_NetSP_High.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7531 | b_ALM_NetSP_Low.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7532 | b_ALM_NetSP_Low.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7533 | b_ALM_NetSP_Low.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7531 | b_ALM_NetSP_Low.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7541 | b_ALM_NetSP_Heartbeat.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7542 | b_ALM_NetSP_Heartbeat.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7543 | b_ALM_NetSP_Heartbeat.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7541 | b_ALM_NetSP_Heartbeat.Count | 2 | Integer | Not currently enabled. | Events
| YES | Discrete Input | 7551 | b_ALM_AnaFlowmeterHigh.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. To continue machine operation, please disable the flowmeter in "Component Configuration" within the "Configuration" menu. Check the flowmeter. Check the analog wiring. | Inactive/Active
| YES | Discrete Input | 7552 | b_ALM_AnaFlowmeterHigh.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7553 | b_ALM_AnaFlowmeterHigh.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7551 | b_ALM_AnaFlowmeterHigh.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7561 | b_ALM_AnaFlowmeterLow.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. To continue machine operation, please disable the flowmeter in "Component Configuration" within the "Configuration" menu. Check the flowmeter. Check the analog wiring. | Inactive/Active
| YES | Discrete Input | 7562 | b_ALM_AnaFlowmeterLow.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7563 | b_ALM_AnaFlowmeterLow.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7561 | b_ALM_AnaFlowmeterLow.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7571 | b_ALM_AnaFlowmeterOther.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. A CHANNEL FAULT has occurred on the FLOWMETER or wiring. To continue machine operation, please disable the flowmeter in "Component Configuration" within the "Configuration" menu. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit. | Inactive/Active
| YES | Discrete Input | 7572 | b_ALM_AnaFlowmeterOther.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7573 | b_ALM_AnaFlowmeterOther.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7571 | b_ALM_AnaFlowmeterOther.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7581 | b_ALM_HighDeviation.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The temperature has deviated too high for too long above the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/blocked cooling valve. Check for a failed (stuck on) heater contactor. | Inactive/Active
| YES | Discrete Input | 7582 | b_ALM_HighDeviation.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7583 | b_ALM_HighDeviation.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7581 | b_ALM_HighDeviation.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7591 | b_ALM_LowDeviation.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The temperature has deviated too low for too long below the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/stuck open cooling valve. Check for a failed heater contactor. | Inactive/Active
| YES | Discrete Input | 7592 | b_ALM_LowDeviation.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7593 | b_ALM_LowDeviation.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7591 | b_ALM_LowDeviation.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7601 | b_ALM_NetworkHeartbeatLost.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The NETWORK HEARTBEAT HAS BEEN LOST after having been initially established. Fix network or remote node. Change Network Timeout action or timeout period. | Inactive/Active
| YES | Discrete Input | 7602 | b_ALM_NetworkHeartbeatLost.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7603 | b_ALM_NetworkHeartbeatLost.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7601 | b_ALM_NetworkHeartbeatLost.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7611 | b_ALM_RemoteSlaveAlarmActive.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. An alarm has been inherrited from banked Slave unit. Rectify the alarm on the banked slave unit. Change the master to not register banked slave alarms. | Inactive/Active
| YES | Discrete Input | 7612 | b_ALM_RemoteSlaveAlarmActive.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7613 | b_ALM_RemoteSlaveAlarmActive.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7611 | b_ALM_RemoteSlaveAlarmActive.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| YES | Discrete Input | 7621 | b_ALM_RampSoakPaused.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. The Ramp/Soak sequence was interrupted by a low pressure condition for too long. The machine will not execute an automatic restart since it would disrupt the sensitive Ramp/Soak sequence that it was attempting to execute. | Inactive/Active
| YES | Discrete Input | 7622 | b_ALM_RampSoakPaused.Enable | 1 | Bool | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| YES | Discrete Input | 7623 | b_ALM_RampSoakPaused.AutoReset | 1 | Bool | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| YES | Input Register | 7621 | b_ALM_RampSoakPaused.Count | 2 | Integer | Number of times .Value has been triggered. | Events
| NO | Discrete Input | 7631 | b_ALM_PID_AT_InitOutputTooHigh.Value | 1 | Bool | This bit signifies whether or not this alarm is currently active. PID autotune's starting control output is too high. Autotune cannot complete successfully. Existing PID settings will remain untouched. TBD TBD | Inactive/Active
| NO | Discrete Input | 7632 | b_ALM_PID_AT_InitOutputTooHigh.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7633 | b_ALM_PID_AT_InitOutputTooHigh.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7631 | b_ALM_PID_AT_InitOutputTooHigh.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7641 | b_ALM_PID_AT_ProcResponseSlow.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7642 | b_ALM_PID_AT_ProcResponseSlow.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7643 | b_ALM_PID_AT_ProcResponseSlow.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7641 | b_ALM_PID_AT_ProcResponseSlow.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7651 | b_ALM_PID_AT_TimeConstNotFound.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7652 | b_ALM_PID_AT_TimeConstNotFound.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7653 | b_ALM_PID_AT_TimeConstNotFound.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7651 | b_ALM_PID_AT_TimeConstNotFound.Count | 2 | Integer | Not currently enabled. | Events
| NO | Discrete Input | 7661 | b_ALM_PID_AT_ProcLimitExceeded.Value | 1 | Bool | Not currently enabled. | Inactive/Active
| NO | Discrete Input | 7662 | b_ALM_PID_AT_ProcLimitExceeded.Enable | 1 | Bool | Not currently enabled. | Disabled/Enabled
| NO | Discrete Input | 7663 | b_ALM_PID_AT_ProcLimitExceeded.AutoReset | 1 | Bool | Not currently enabled. | Manual/Auto
| NO | Input Register | 7661 | b_ALM_PID_AT_ProcLimitExceeded.Count | 2 | Integer | Not currently enabled. | Events
Hardware Digital Inputs, intended for individual read only as necessary.
| YES | Discrete Input | 8000 | b_IN_PressureSwitch.Value | 1 | Bool | Status of pressure switch on return (from process) side of process loop. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8001 | b_IN_PressureSwitch.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8000 | b_IN_PressureSwitch.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8010 | b_IN_PumpContactorAux.Value | 1 | Bool | Status of the pump contactor, as indicated by a set of auxiliary contacts on the contactor. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8011 | b_IN_PumpContactorAux.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8010 | b_IN_PumpContactorAux.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8020 | b_IN_PumpOverload.Value | 1 | Bool | Status of pump overload. No overload = TRUE; Tripped overload = FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8021 | b_IN_PumpOverload.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8020 | b_IN_PumpOverload.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8030 | b_IN_HeaterContactorAux.Value | 1 | Bool | Status of the pump contactor, as indicated by a set of auxiliary contacts on the contactor. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8031 | b_IN_HeaterContactorAux.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8030 | b_IN_HeaterContactorAux.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8040 | b_IN_PhaseMonitor.Value | 1 | Bool | Status of phase monitor. Phases OK=TRUE; Phase Error=FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8041 | b_IN_PhaseMonitor.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8040 | b_IN_PhaseMonitor.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8050 | b_IN_HeaterHighTemp.Value | 1 | Bool | Status of an external high temperature switch. Temp OK=TRUE; Overtemp=FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8051 | b_IN_HeaterHighTemp.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8050 | b_IN_HeaterHighTemp.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8060 | b_IN_Flowswitch.Value | 1 | Bool | Status of flowswitch in the process loop. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8061 | b_IN_Flowswitch.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8060 | b_IN_Flowswitch.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8070 | b_IN_RemoteStart.Value | 1 | Bool | Status of remote start input. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8071 | b_IN_RemoteStart.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8070 | b_IN_RemoteStart.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
| YES | Discrete Input | 8080 | b_IN_SetpointSelectAdvance.Value | 1 | Bool | Status of Setpoint Select / Ramp/Soak Step Advance input. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 8081 | b_IN_SetpointSelectAdvance.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8080 | b_IN_SetpointSelectAdvance.Error | 2 | Integer | 10=No error, 0=Error. | <enumeration>
Hardware Analog Inputs, intended for individual read only as necessary.
| YES | Input Register | 8500 | r_IN_SupplyRTD.Value | 2 | Floating point | Value of Supply (To Process) RTD input. In units of degrees Celsius (°C). Offset according to calibration parameter(s). Only valid if .Implemented is TRUE, and .Error is "10". | °C
| YES | Discrete Input | 8500 | r_IN_SupplyRTD.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8502 | r_IN_SupplyRTD.Error | 2 | Integer | 0=Not in use; -2=Probe Short Circuit; -1=Probe not connected; 10=No error | <enumeration>
| YES | Input Register | 8510 | r_IN_ReturnRTD.Value | 2 | Floating point | Value of Return (From Process) RTD input. In units of degrees Celsius (°C). Offset according to calibration parameter(s). Only valid if .Implemented is TRUE, and .Error is "10". | °C
| YES | Discrete Input | 8510 | r_IN_ReturnRTD.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8512 | r_IN_ReturnRTD.Error | 2 | Integer | 0=Not in use; -2=Probe Short Circuit; -1=Probe not connected; 10=No error | <enumeration>
| YES | Input Register | 8520 | r_IN_RemoteRTD.Value | 2 | Floating point | Value of Remote RTD input. In units of degrees Celsius (°C). Offset according to calibration parameter(s). Only valid if .Implemented is TRUE, and .Error is "10". | °C
| YES | Discrete Input | 8520 | r_IN_RemoteRTD.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8522 | r_IN_RemoteRTD.Error | 2 | Integer | 0=Not in use; -2=Probe Short Circuit; -1=Probe not connected; 10=No error | <enumeration>
| YES | Input Register | 8530 | r_IN_SupplyPressure.Value | 2 | Floating point | Value of Supply (To Process) input. In units of pounds per square inch (psi). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | psi
| YES | Discrete Input | 8530 | r_IN_SupplyPressure.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8532 | r_IN_SupplyPressure.Error | 2 | Integer | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Sensor not connected; 10=No error | <enumeration>
| YES | Input Register | 8540 | r_IN_ReturnPressure.Value | 2 | Floating point | Value of Return (From Process) input. In units of pounds per square inch (psi). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | psi
| YES | Discrete Input | 8540 | r_IN_ReturnPressure.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8542 | r_IN_ReturnPressure.Error | 2 | Integer | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Sensor not connected; 10=No error | <enumeration>
| NO | Input Register | 8550 | r_IN_AnalogSetpoint.Value | 2 | Floating point | Not currently implemented. | °C
| NO | Discrete Input | 8550 | r_IN_AnalogSetpoint.Implemented | 1 | Bool | Not currently implemented. | On/Off
| NO | Input Register | 8552 | r_IN_AnalogSetpoint.Error | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Input Register | 8560 | r_IN_AnalogFlowmeter.Value | 2 | Floating point | Value of Analog Flowmeter input. In units of gallons per minute (gpm). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | °C
| YES | Discrete Input | 8560 | r_IN_AnalogFlowmeter.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8562 | r_IN_AnalogFlowmeter.Error | 2 | Integer | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Flowmeter not connected; 10=No error | <enumeration>
| NO | Input Register | 8570 | r_IN_AnalogProcess.Value | 2 | Floating point | Not currently implemented. | °C
| NO | Discrete Input | 8570 | r_IN_AnalogProcess.Implemented | 1 | Bool | Not currently implemented. | On/Off
| NO | Input Register | 8572 | r_IN_AnalogProcess.Error | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Input Register | 8580 | r_IN_RemoteResistorControl.Value | 2 | Floating point | Value of remote resistor control input. In units of ohms (Ω). Only valid if .Implemented is TRUE, and .Error is "10". | ohms
| YES | Discrete Input | 8580 | r_IN_RemoteResistorControl.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8582 | r_IN_RemoteResistorControl.Error | 2 | Integer | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Nothing connected; 10=No error | <enumeration>
| YES | Input Register | 8590 | r_IN_ElecEnclosureTemp.Value | 2 | Floating point | Value of enclosure temperature input. In units of degrees Celsius (°C). Only valid if .Implemented is TRUE, and .Error is "10". | °C
| YES | Discrete Input | 8590 | r_IN_ElecEnclosureTemp.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8592 | r_IN_ElecEnclosureTemp.Error | 2 | Integer | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Sensor not connected; 10=No error | <enumeration>
| YES | Input Register | 8600 | r_IN_PulseFlowmeter.Value | 2 | Floating point | Value of pulse flowmeter input in the process loop. In units of gallon per minute (gpm). K-Factor is already applied to this number. Only valid if .Implemented is TRUE, and .Error is "10". | gpm
| YES | Discrete Input | 8600 | r_IN_PulseFlowmeter.Implemented | 1 | Bool | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 8602 | r_IN_PulseFlowmeter.Error | 2 | Integer | 0=Not in use; 10=No error | <enumeration>
Hardware Digital Outputs, intended for individual read only as necessary.
| YES | Discrete Input | 9000 | b_OUT_PumpContactor.Value | 1 | Bool | Status of pump contactor output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9001 | b_OUT_PumpContactor.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9000 | b_OUT_PumpContactor.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9010 | b_OUT_HeaterContactor.Value | 1 | Bool | Status of heater electromechanical contactor output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9011 | b_OUT_HeaterContactor.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9010 | b_OUT_HeaterContactor.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9020 | b_OUT_HeaterSSR.Value | 1 | Bool | Status of heater SSR output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9021 | b_OUT_HeaterSSR.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9020 | b_OUT_HeaterSSR.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9030 | b_OUT_CoolingValveOpen.Value | 1 | Bool | Status of cooling valve (open) output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9031 | b_OUT_CoolingValveOpen.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9030 | b_OUT_CoolingValveOpen.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9040 | b_OUT_MoldPurge.Value | 1 | Bool | Status of mold purge solenoid valve output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9041 | b_OUT_MoldPurge.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9040 | b_OUT_MoldPurge.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9050 | b_OUT_AlarmSilenceable.Value | 1 | Bool | Status of silenceable alarm output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9051 | b_OUT_AlarmSilenceable.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9050 | b_OUT_AlarmSilenceable.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9060 | b_OUT_AlarmNonSilenceable.Value | 1 | Bool | Status of non-silenceable alarm output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9061 | b_OUT_AlarmNonSilenceable.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9060 | b_OUT_AlarmNonSilenceable.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9070 | b_OUT_Vent.Value | 1 | Bool | Status of vent solenoid output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9071 | b_OUT_Vent.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9070 | b_OUT_Vent.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| YES | Discrete Input | 9080 | b_OUT_FillValve.Value | 1 | Bool | Status of fill solenoid output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off
| YES | Discrete Input | 9081 | b_OUT_FillValve.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9080 | b_OUT_FillValve.Error | 2 | Integer | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
Hardware Analog Outputs, intended for individual read only as necessary.
| YES | Input Register | 9500 | r_OUT_ModulatingCoolingValve.Value | 2 | Floating point | Value of analog output for cooling modulating valve. In units of percent (%). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | %
| YES | Discrete Input | 9500 | r_OUT_ModulatingCoolingValve.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9502 | r_OUT_ModulatingCoolingValve.Error | 2 | Integer | 0=Not in use; 10=No error | <enumeration>
| YES | Input Register | 9510 | r_OUT_AnalogProcessRetransmit.Value | 2 | Floating point | Value of analog output for process value retransmit. In units of degrees Celsius (°C). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | °C
| YES | Discrete Input | 9510 | r_OUT_AnalogProcessRetransmit.Implemented | 1 | Bool | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| YES | Input Register | 9512 | r_OUT_AnalogProcessRetransmit.Error | 2 | Integer | 0=Not in use; 10=No error | <enumeration>
Ramp/Soak, intended for individual read/write only as necessary.
| YES | Input Register | 10000 | n_RampSoakMaxSteps | 1 | Integer | Maximum number of steps permitted for Ramp/Soak | steps
| YES | Input Register | 10001 | st_NET_RampSoakRecipe.InterimSetpointSts | 2 | Floating point | The interim setpoint if the step is time-limited or rate-limited. In units of °C. | °C
| YES | Input Register | 10003 | st_NET_RampSoakRecipe.NextActionCountdown | 1 | Integer | Time countdown for the next action in a ramp/soak sequence. In units of seconds. | seconds
| YES | Discrete Input | 10100 | st_NET_RampSoakRecipe.Steps[1].LimitStartsAtPV | 1 | Bool | Step #1: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step (first step based on process value at unit startup). | No/Yes
| YES | Input Register | 10100 | st_NET_RampSoakRecipe.Steps[1].NextAction | 1 | Integer | Step #1: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Input Register | 10101 | st_NET_RampSoakRecipe.Steps[1].NextStep | 1 | Integer | Step #1: The next step number (if applicable, based on next action). | <enumeration>
| YES | Input Register | 10102 | st_NET_RampSoakRecipe.Steps[1].Setpoint | 2 | Floating point | Step #1: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 10101 | st_NET_RampSoakRecipe.Steps[1].StepActive | 1 | Bool | Step #1: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Input Register | 10104 | st_NET_RampSoakRecipe.Steps[1].StepDuration | 2 | Integer | Step #1: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Input Register | 10106 | st_NET_RampSoakRecipe.Steps[1].TempRateLimit | 2 | Floating point | Step #1: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Input Register | 10108 | st_NET_RampSoakRecipe.Steps[1].TimedRateLimit | 2 | Integer | Step #1: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Input Register | 10110 | st_NET_RampSoakRecipe.Steps[1].TriggerForNext | 1 | Integer | Step #1: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Discrete Input | 10200 | st_NET_RampSoakRecipe.Steps[2].LimitStartsAtPV | 1 | Bool | Step #2: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Input Register | 10200 | st_NET_RampSoakRecipe.Steps[2].NextAction | 1 | Integer | Step #2: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Input Register | 10201 | st_NET_RampSoakRecipe.Steps[2].NextStep | 1 | Integer | Step #2: The next step number (if applicable, based on next action). | <enumeration>
| YES | Input Register | 10202 | st_NET_RampSoakRecipe.Steps[2].Setpoint | 2 | Floating point | Step #2: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 10201 | st_NET_RampSoakRecipe.Steps[2].StepActive | 1 | Bool | Step #2: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Input Register | 10204 | st_NET_RampSoakRecipe.Steps[2].StepDuration | 2 | Integer | Step #2: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Input Register | 10206 | st_NET_RampSoakRecipe.Steps[2].TempRateLimit | 2 | Floating point | Step #2: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Input Register | 10208 | st_NET_RampSoakRecipe.Steps[2].TimedRateLimit | 2 | Integer | Step #2: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Input Register | 10210 | st_NET_RampSoakRecipe.Steps[2].TriggerForNext | 1 | Integer | Step #2: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Discrete Input | 10300 | st_NET_RampSoakRecipe.Steps[3].LimitStartsAtPV | 1 | Bool | Step #3: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Input Register | 10300 | st_NET_RampSoakRecipe.Steps[3].NextAction | 1 | Integer | Step #3: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Input Register | 10301 | st_NET_RampSoakRecipe.Steps[3].NextStep | 1 | Integer | Step #3: The next step number (if applicable, based on next action). | <enumeration>
| YES | Input Register | 10302 | st_NET_RampSoakRecipe.Steps[3].Setpoint | 2 | Floating point | Step #3: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 10301 | st_NET_RampSoakRecipe.Steps[3].StepActive | 1 | Bool | Step #3: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Input Register | 10304 | st_NET_RampSoakRecipe.Steps[3].StepDuration | 2 | Integer | Step #3: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Input Register | 10306 | st_NET_RampSoakRecipe.Steps[3].TempRateLimit | 2 | Floating point | Step #3: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Input Register | 10308 | st_NET_RampSoakRecipe.Steps[3].TimedRateLimit | 2 | Integer | Step #3: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Input Register | 10310 | st_NET_RampSoakRecipe.Steps[3].TriggerForNext | 1 | Integer | Step #3: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Discrete Input | 10400 | st_NET_RampSoakRecipe.Steps[4].LimitStartsAtPV | 1 | Bool | Step #4: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Input Register | 10400 | st_NET_RampSoakRecipe.Steps[4].NextAction | 1 | Integer | Step #4: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Input Register | 10401 | st_NET_RampSoakRecipe.Steps[4].NextStep | 1 | Integer | Step #4: The next step number (if applicable, based on next action). | <enumeration>
| YES | Input Register | 10402 | st_NET_RampSoakRecipe.Steps[4].Setpoint | 2 | Floating point | Step #4: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 10401 | st_NET_RampSoakRecipe.Steps[4].StepActive | 1 | Bool | Step #4: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Input Register | 10404 | st_NET_RampSoakRecipe.Steps[4].StepDuration | 2 | Integer | Step #4: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Input Register | 10406 | st_NET_RampSoakRecipe.Steps[4].TempRateLimit | 2 | Floating point | Step #4: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Input Register | 10408 | st_NET_RampSoakRecipe.Steps[4].TimedRateLimit | 2 | Integer | Step #4: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Input Register | 10410 | st_NET_RampSoakRecipe.Steps[4].TriggerForNext | 1 | Integer | Step #4: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Discrete Input | 10500 | st_NET_RampSoakRecipe.Steps[5].LimitStartsAtPV | 1 | Bool | Step #5: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Input Register | 10500 | st_NET_RampSoakRecipe.Steps[5].NextAction | 1 | Integer | Step #5: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Input Register | 10501 | st_NET_RampSoakRecipe.Steps[5].NextStep | 1 | Integer | Step #5: The next step number (if applicable, based on next action). | <enumeration>
| YES | Input Register | 10502 | st_NET_RampSoakRecipe.Steps[5].Setpoint | 2 | Floating point | Step #5: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 10501 | st_NET_RampSoakRecipe.Steps[5].StepActive | 1 | Bool | Step #5: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Input Register | 10504 | st_NET_RampSoakRecipe.Steps[5].StepDuration | 2 | Integer | Step #5: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Input Register | 10506 | st_NET_RampSoakRecipe.Steps[5].TempRateLimit | 2 | Floating point | Step #5: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Input Register | 10508 | st_NET_RampSoakRecipe.Steps[5].TimedRateLimit | 2 | Integer | Step #5: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Input Register | 10510 | st_NET_RampSoakRecipe.Steps[5].TriggerForNext | 1 | Integer | Step #5: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Discrete Input | 11000 | b_RampSoakRecipe_RemWriteAccess | 1 | Bool | FALSE=The ramp/soak recipe is currently read-only; TRUE=The ramp/soak recipie can be currently changed via the "To Set" parameters. | No/Yes
| YES | Coil | 11000 | b_RampSoakRecipe_WriteRemoteData | 1 | Bool | Set TRUE to load the "To Set" data into the current recipie. | No/Yes
| YES | Coil | 11100 | st_RampSoakRecipeToSet.Steps[1].LimitStartsAtPV | 1 | Bool | Step #1 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step (first step based on process value at unit startup). | No/Yes
| YES | Holding Register | 11100 | st_RampSoakRecipeToSet.Steps[1].NextAction | 1 | Integer | Step #1 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Holding Register | 11101 | st_RampSoakRecipeToSet.Steps[1].NextStep | 1 | Integer | Step #1 to set: The next step number (if applicable, based on next action). | <enumeration>
| YES | Holding Register | 11102 | st_RampSoakRecipeToSet.Steps[1].Setpoint | 2 | Floating point | Step #1 to set: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 11100 | st_RampSoakRecipeToSet.Steps[1].StepActive | 1 | Bool | Step #1 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Holding Register | 11104 | st_RampSoakRecipeToSet.Steps[1].StepDuration | 2 | Integer | Step #1 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Holding Register | 11106 | st_RampSoakRecipeToSet.Steps[1].TempRateLimit | 2 | Floating point | Step #1 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Holding Register | 11108 | st_RampSoakRecipeToSet.Steps[1].TimedRateLimit | 2 | Integer | Step #1 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Holding Register | 11110 | st_RampSoakRecipeToSet.Steps[1].TriggerForNext | 1 | Integer | Step #1 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Coil | 11200 | st_RampSoakRecipeToSet.Steps[2].LimitStartsAtPV | 1 | Bool | Step #2 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Holding Register | 11200 | st_RampSoakRecipeToSet.Steps[2].NextAction | 1 | Integer | Step #2 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Holding Register | 11201 | st_RampSoakRecipeToSet.Steps[2].NextStep | 1 | Integer | Step #2 to set: The next step number (if applicable, based on next action). | <enumeration>
| YES | Holding Register | 11202 | st_RampSoakRecipeToSet.Steps[2].Setpoint | 2 | Floating point | Step #2 to set: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 11200 | st_RampSoakRecipeToSet.Steps[2].StepActive | 1 | Bool | Step #2 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Holding Register | 11204 | st_RampSoakRecipeToSet.Steps[2].StepDuration | 2 | Integer | Step #2 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Holding Register | 11206 | st_RampSoakRecipeToSet.Steps[2].TempRateLimit | 2 | Floating point | Step #2 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Holding Register | 11208 | st_RampSoakRecipeToSet.Steps[2].TimedRateLimit | 2 | Integer | Step #2 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Holding Register | 11210 | st_RampSoakRecipeToSet.Steps[2].TriggerForNext | 1 | Integer | Step #2 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Coil | 11300 | st_RampSoakRecipeToSet.Steps[3].LimitStartsAtPV | 1 | Bool | Step #3 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Holding Register | 11300 | st_RampSoakRecipeToSet.Steps[3].NextAction | 1 | Integer | Step #3 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Holding Register | 11301 | st_RampSoakRecipeToSet.Steps[3].NextStep | 1 | Integer | Step #3 to set: The next step number (if applicable, based on next action). | <enumeration>
| YES | Holding Register | 11302 | st_RampSoakRecipeToSet.Steps[3].Setpoint | 2 | Floating point | Step #3 to set: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 11300 | st_RampSoakRecipeToSet.Steps[3].StepActive | 1 | Bool | Step #3 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Holding Register | 11304 | st_RampSoakRecipeToSet.Steps[3].StepDuration | 2 | Integer | Step #3 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Holding Register | 11306 | st_RampSoakRecipeToSet.Steps[3].TempRateLimit | 2 | Floating point | Step #3 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Holding Register | 11308 | st_RampSoakRecipeToSet.Steps[3].TimedRateLimit | 2 | Integer | Step #3 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Holding Register | 11310 | st_RampSoakRecipeToSet.Steps[3].TriggerForNext | 1 | Integer | Step #3 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Coil | 11400 | st_RampSoakRecipeToSet.Steps[4].LimitStartsAtPV | 1 | Bool | Step #4 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Holding Register | 11400 | st_RampSoakRecipeToSet.Steps[4].NextAction | 1 | Integer | Step #4 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Holding Register | 11401 | st_RampSoakRecipeToSet.Steps[4].NextStep | 1 | Integer | Step #4 to set: The next step number (if applicable, based on next action). | <enumeration>
| YES | Holding Register | 11402 | st_RampSoakRecipeToSet.Steps[4].Setpoint | 2 | Floating point | Step #4 to set: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 11400 | st_RampSoakRecipeToSet.Steps[4].StepActive | 1 | Bool | Step #4 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Holding Register | 11404 | st_RampSoakRecipeToSet.Steps[4].StepDuration | 2 | Integer | Step #4 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Holding Register | 11406 | st_RampSoakRecipeToSet.Steps[4].TempRateLimit | 2 | Floating point | Step #4 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Holding Register | 11408 | st_RampSoakRecipeToSet.Steps[4].TimedRateLimit | 2 | Integer | Step #4 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Holding Register | 11410 | st_RampSoakRecipeToSet.Steps[4].TriggerForNext | 1 | Integer | Step #4 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| YES | Coil | 11500 | st_RampSoakRecipeToSet.Steps[5].LimitStartsAtPV | 1 | Bool | Step #5 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| YES | Holding Register | 11500 | st_RampSoakRecipeToSet.Steps[5].NextAction | 1 | Integer | Step #5 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| YES | Holding Register | 11501 | st_RampSoakRecipeToSet.Steps[5].NextStep | 1 | Integer | Step #5 to set: The next step number (if applicable, based on next action). | <enumeration>
| YES | Holding Register | 11502 | st_RampSoakRecipeToSet.Steps[5].Setpoint | 2 | Floating point | Step #5 to set: Setpoint of the step. In units of °C. | °C
| YES | Discrete Input | 11500 | st_RampSoakRecipeToSet.Steps[5].StepActive | 1 | Bool | Step #5 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| YES | Holding Register | 11504 | st_RampSoakRecipeToSet.Steps[5].StepDuration | 2 | Integer | Step #5 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| YES | Holding Register | 11506 | st_RampSoakRecipeToSet.Steps[5].TempRateLimit | 2 | Floating point | Step #5 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| YES | Holding Register | 11508 | st_RampSoakRecipeToSet.Steps[5].TimedRateLimit | 2 | Integer | Step #5 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| YES | Holding Register | 11510 | st_RampSoakRecipeToSet.Steps[5].TriggerForNext | 1 | Integer | Step #5 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
HMI Display Values, intended for individual read only as necessary.
| YES | Discrete Input | 12000 | r_HD_SupplyTemp.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12000 | r_HD_SupplyTemp.Value | 2 | Floating point | This is the value shown on the touchscreen for "To Process Temperature". In units of °C. | °C
| YES | Input Register | 12002 | r_HD_SupplyTemp.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12004 | r_HD_SupplyTemp.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12006 | r_HD_SupplyTemp.Error | 2 | Integer | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12010 | r_HD_ReturnTemp.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12010 | r_HD_ReturnTemp.Value | 2 | Floating point | This is the value shown on the touchscreen for "From Process Temperature". In units of °C. | °C
| YES | Input Register | 12012 | r_HD_ReturnTemp.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12014 | r_HD_ReturnTemp.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12016 | r_HD_ReturnTemp.Error | 2 | Integer | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12020 | r_HD_SupplyReturnAvgTemp.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12020 | r_HD_SupplyReturnAvgTemp.Value | 2 | Floating point | This is the value shown on the touchscreen for "To/From Average Temperature". In units °C. | °C
| YES | Input Register | 12022 | r_HD_SupplyReturnAvgTemp.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12024 | r_HD_SupplyReturnAvgTemp.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12026 | r_HD_SupplyReturnAvgTemp.Error | 2 | Integer | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12030 | r_HD_RemoteTemp.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12030 | r_HD_RemoteTemp.Value | 2 | Floating point | This is the value shown on the touchscreen for "Remote Temperature". In units of °C. | °C
| YES | Input Register | 12032 | r_HD_RemoteTemp.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12034 | r_HD_RemoteTemp.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12036 | r_HD_RemoteTemp.Error | 2 | Integer | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12040 | r_HD_Flowrate.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12040 | r_HD_Flowrate.Value | 2 | Floating point | This is the value shown on the touchscreen for "Flowrate (analog)". In units of gpm. | gpm
| YES | Input Register | 12042 | r_HD_Flowrate.Minimum | 2 | Floating point | The minimum permitted value. | gpm
| YES | Input Register | 12044 | r_HD_Flowrate.Maximum | 2 | Floating point | The maximum permitted value. | gpm
| YES | Input Register | 12046 | r_HD_Flowrate.Error | 2 | Integer | Describes if value is valid: 10=No Error; 5=High Circuit Fault; 6=Low Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12050 | r_HD_EstimatedFlowrate.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12050 | r_HD_EstimatedFlowrate.Value | 2 | Floating point | This is the value shown on the touchscreen for "Estimated Flowrate". In units of gpm. | gpm
| YES | Input Register | 12052 | r_HD_EstimatedFlowrate.Minimum | 2 | Floating point | The minimum permitted value. | gpm
| YES | Input Register | 12054 | r_HD_EstimatedFlowrate.Maximum | 2 | Floating point | The maximum permitted value. | gpm
| YES | Input Register | 12056 | r_HD_EstimatedFlowrate.Error | 2 | Integer | Describes if value is valid: 10=No Error; 3=Not Currently Active; 8=No Calibration Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12060 | r_HD_SupplyPress.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12060 | r_HD_SupplyPress.Value | 2 | Floating point | This is the value shown on the touchscreen for "To Process Pressure". In units of psi. | psi
| YES | Input Register | 12062 | r_HD_SupplyPress.Minimum | 2 | Floating point | The minimum permitted value. | psi
| YES | Input Register | 12064 | r_HD_SupplyPress.Maximum | 2 | Floating point | The maximum permitted value. | psi
| YES | Input Register | 12066 | r_HD_SupplyPress.Error | 2 | Integer | Describes if value is valid: 10=No Error; 5=High Circuit Fault; 6=Low Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12070 | r_HD_ReturnPress.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12070 | r_HD_ReturnPress.Value | 2 | Floating point | This is the value shown on the touchscreen for "From Process Pressure". In units of psi. | psi
| YES | Input Register | 12072 | r_HD_ReturnPress.Minimum | 2 | Floating point | The minimum permitted value. | psi
| YES | Input Register | 12074 | r_HD_ReturnPress.Maximum | 2 | Floating point | The maximum permitted value. | psi
| YES | Input Register | 12076 | r_HD_ReturnPress.Error | 2 | Integer | Describes if value is valid: 10=No Error; 5=High Circuit Fault; 6=Low Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12080 | r_HD_HeatCool_Pct.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12080 | r_HD_HeatCool_Pct.Value | 2 | Floating point | This is the value shown on the touchscreen for "Heat / Cool Amount (Instantaneous)". In units of %. | %
| YES | Input Register | 12082 | r_HD_HeatCool_Pct.Minimum | 2 | Floating point | The minimum permitted value. | %
| YES | Input Register | 12084 | r_HD_HeatCool_Pct.Maximum | 2 | Floating point | The maximum permitted value. | %
| YES | Input Register | 12086 | r_HD_HeatCool_Pct.Error | 2 | Integer | Describes if value is valid: 10=0% Heat/Cool; 0=Heat/Cool Off; 1=Heating, 2=Cooling, 3=Maximum Cooling. | <enumeration>
| YES | Discrete Input | 12090 | r_HD_Heat_Pct.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12090 | r_HD_Heat_Pct.Value | 2 | Floating point | This is the value shown on the touchscreen for "Heat Amount (Instantaneous)". In units of %. | %
| YES | Input Register | 12092 | r_HD_Heat_Pct.Minimum | 2 | Floating point | The minimum permitted value. | %
| YES | Input Register | 12094 | r_HD_Heat_Pct.Maximum | 2 | Floating point | The maximum permitted value. | %
| YES | Input Register | 12096 | r_HD_Heat_Pct.Error | 2 | Integer | Describes if value is valid: 10=No error; 0=Error | <enumeration>
| YES | Discrete Input | 12100 | r_HD_Cool_Pct.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12100 | r_HD_Cool_Pct.Value | 2 | Floating point | This is the value shown on the touchscreen for "Cool Amount (Instantaneous)". In units of %. | %
| YES | Input Register | 12102 | r_HD_Cool_Pct.Minimum | 2 | Floating point | The minimum permitted value. | %
| YES | Input Register | 12104 | r_HD_Cool_Pct.Maximum | 2 | Floating point | The maximum permitted value. | %
| YES | Input Register | 12106 | r_HD_Cool_Pct.Error | 2 | Integer | Describes if value is valid: 10=No error; 0=Error | <enumeration>
| NO | Discrete Input | 12110 | r_HD_NetworkProcessTemp.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12110 | r_HD_NetworkProcessTemp.Value | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12112 | r_HD_NetworkProcessTemp.Minimum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12114 | r_HD_NetworkProcessTemp.Maximum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12116 | r_HD_NetworkProcessTemp.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 12120 | r_HD_AnalogProcessTemp.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12120 | r_HD_AnalogProcessTemp.Value | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12122 | r_HD_AnalogProcessTemp.Minimum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12124 | r_HD_AnalogProcessTemp.Maximum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12126 | r_HD_AnalogProcessTemp.Error | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Discrete Input | 12130 | r_HD_ActiveProcTemp.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12130 | r_HD_ActiveProcTemp.Value | 2 | Floating point | This is the value shown on the touchscreen for "Active Process Temperature". Units of °C. | °C
| YES | Input Register | 12132 | r_HD_ActiveProcTemp.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12134 | r_HD_ActiveProcTemp.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12136 | r_HD_ActiveProcTemp.Error | 2 | Integer | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| YES | Discrete Input | 12140 | r_HD_RampSoakSetpoint.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12140 | r_HD_RampSoakSetpoint.Value | 2 | Floating point | This is the value shown on the touchscreen for "Ramp/Soak Setpoint". In units of °C. | °C
| YES | Input Register | 12142 | r_HD_RampSoakSetpoint.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12144 | r_HD_RampSoakSetpoint.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12146 | r_HD_RampSoakSetpoint.Error | 2 | Integer | Describes if value is valid: 10=No Error; 4=Not Used; 0=Error. | <enumeration>
| NO | Discrete Input | 12150 | r_HD_AnalogSetpoint.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12150 | r_HD_AnalogSetpoint.Value | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12152 | r_HD_AnalogSetpoint.Minimum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12154 | r_HD_AnalogSetpoint.Maximum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12156 | r_HD_AnalogSetpoint.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 12160 | r_HD_NetworkSetpoint.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12160 | r_HD_NetworkSetpoint.Value | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12162 | r_HD_NetworkSetpoint.Minimum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12164 | r_HD_NetworkSetpoint.Maximum | 2 | Floating point | Not currently implemented. | °C
| NO | Input Register | 12166 | r_HD_NetworkSetpoint.Error | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Discrete Input | 12170 | r_HD_SuggestedSetpoint.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12170 | r_HD_SuggestedSetpoint.Value | 2 | Floating point | This is the value shown on the touchscreen for suggested setpoint if pressure too low. In units of °C. | °C
| YES | Input Register | 12172 | r_HD_SuggestedSetpoint.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12174 | r_HD_SuggestedSetpoint.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12176 | r_HD_SuggestedSetpoint.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Value not currently useful; 0=Error. | <enumeration>
| YES | Discrete Input | 12180 | r_HD_EffectiveProcValue.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12180 | r_HD_EffectiveProcValue.Value | 2 | Floating point | This is the value shown on the touchscreen for the process value being used to drive the PID loop. In units of °C. | °C
| YES | Input Register | 12182 | r_HD_EffectiveProcValue.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12184 | r_HD_EffectiveProcValue.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12186 | r_HD_EffectiveProcValue.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12190 | n_HD_EffectiveProcValueSource.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12190 | n_HD_EffectiveProcValueSource.Value | 2 | Integer | This is the value shown on the touchscreen for the enumerated source for the filtered effective process value. 0="To Process RTD", 1="From Process RTD", 2="To/From RTD Avg", 3="Remote RTD", 4="Analog Signal", 5="Network" | <enumeration>
| YES | Input Register | 12192 | n_HD_EffectiveProcValueSource.Minimum | 2 | Integer | The minimum permitted value. | <enumeration>
| YES | Input Register | 12194 | n_HD_EffectiveProcValueSource.Maximum | 2 | Integer | The maximum permitted value. | <enumeration>
| YES | Input Register | 12196 | n_HD_EffectiveProcValueSource.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12200 | r_HD_FilteredEffectiveProcValue.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12200 | r_HD_FilteredEffectiveProcValue.Value | 2 | Floating point | This is the value shown on the touchscreen for "Filtered Effective Process Value". In units of °C. | °C
| YES | Input Register | 12202 | r_HD_FilteredEffectiveProcValue.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12204 | r_HD_FilteredEffectiveProcValue.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12206 | r_HD_FilteredEffectiveProcValue.Error | 2 | Integer | Describes if value is valid: 10=No Error; 3=Selected Setpoint Source is providing a bad value; 0=Error. | <enumeration>
| YES | Discrete Input | 12210 | r_HD_EffectiveSetpoint.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12210 | r_HD_EffectiveSetpoint.Value | 2 | Floating point | This is the value shown on the touchscreen for the setpoint value being used to drive the PID loop. In units of °C. | °C
| YES | Input Register | 12212 | r_HD_EffectiveSetpoint.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12214 | r_HD_EffectiveSetpoint.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12216 | r_HD_EffectiveSetpoint.Error | 2 | Integer | Describes if value is valid: 10=No Error; 4=Not Used; 5=High Circuit Fault; 6=Low Circuit Fault; 7=Heartbeat Error; 3=Other Fault; 0=Error. | <enumeration>
| YES | Discrete Input | 12220 | n_HD_EffectiveSetpointSource.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12220 | n_HD_EffectiveSetpointSource.Value | 2 | Integer | This is the value shown on the touchscreen for the enumerated source for the effective setpoint value. 0=Main; 1=Alternative; 2=Ramp/Soak; 3=Analog Signal; 4=Network | <enumeration>
| YES | Input Register | 12222 | n_HD_EffectiveSetpointSource.Minimum | 2 | Integer | The minimum permitted value. | <enumeration>
| YES | Input Register | 12224 | n_HD_EffectiveSetpointSource.Maximum | 2 | Integer | The maximum permitted value. | <enumeration>
| YES | Input Register | 12226 | n_HD_EffectiveSetpointSource.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12230 | r_HD_PID_Multiplier.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12230 | r_HD_PID_Multiplier.Value | 2 | Floating point | This is the value shown on the touchscreen for the modification factor on the PID output to compensate for non-linearities in the system. | N/A
| YES | Input Register | 12232 | r_HD_PID_Multiplier.Minimum | 2 | Floating point | The minimum permitted value. | N/A
| YES | Input Register | 12234 | r_HD_PID_Multiplier.Maximum | 2 | Floating point | The maximum permitted value. | N/A
| YES | Input Register | 12236 | r_HD_PID_Multiplier.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| YES | Discrete Input | 12240 | r_HD_PID_ProportionalTerm.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12240 | r_HD_PID_ProportionalTerm.Value | 2 | Floating point | This is the value shown on the touchscreen for the proportional contribution from the PID loop. In units of %. | %
| YES | Input Register | 12242 | r_HD_PID_ProportionalTerm.Minimum | 2 | Floating point | The minimum permitted value. | %
| YES | Input Register | 12244 | r_HD_PID_ProportionalTerm.Maximum | 2 | Floating point | The maximum permitted value. | %
| YES | Input Register | 12246 | r_HD_PID_ProportionalTerm.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| YES | Discrete Input | 12250 | r_HD_PID_IntegralTerm.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12250 | r_HD_PID_IntegralTerm.Value | 2 | Floating point | This is the value shown on the touchscreen for the integral contribution from the PID loop. In units of %. | %
| YES | Input Register | 12252 | r_HD_PID_IntegralTerm.Minimum | 2 | Floating point | The minimum permitted value. | %
| YES | Input Register | 12254 | r_HD_PID_IntegralTerm.Maximum | 2 | Floating point | The maximum permitted value. | %
| YES | Input Register | 12256 | r_HD_PID_IntegralTerm.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| YES | Discrete Input | 12260 | r_HD_PID_DerivativeTerm.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12260 | r_HD_PID_DerivativeTerm.Value | 2 | Floating point | This is the value shown on the touchscreen for the derivative contribution from the PID loop. In units of %. | %
| YES | Input Register | 12262 | r_HD_PID_DerivativeTerm.Minimum | 2 | Floating point | The minimum permitted value. | %
| YES | Input Register | 12264 | r_HD_PID_DerivativeTerm.Maximum | 2 | Floating point | The maximum permitted value. | %
| YES | Input Register | 12266 | r_HD_PID_DerivativeTerm.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| YES | Discrete Input | 12270 | r_HD_PID_Error.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12270 | r_HD_PID_Error.Value | 2 | Floating point | This is the value shown on the touchscreen for the difference between the setpoint and the process value from the PID loop. In units of Δ°C. | Δ°C
| YES | Input Register | 12272 | r_HD_PID_Error.Minimum | 2 | Floating point | The minimum permitted value. | Δ°C
| YES | Input Register | 12274 | r_HD_PID_Error.Maximum | 2 | Floating point | The maximum permitted value. | Δ°C
| YES | Input Register | 12276 | r_HD_PID_Error.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| YES | Discrete Input | 12280 | r_HD_PID_RawLoopOutput.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12280 | r_HD_PID_RawLoopOutput.Value | 2 | Floating point | This is the value shown on the touchscreen for the raw output from the PID loop. In units of %. | %
| YES | Input Register | 12282 | r_HD_PID_RawLoopOutput.Minimum | 2 | Floating point | The minimum permitted value. | %
| YES | Input Register | 12284 | r_HD_PID_RawLoopOutput.Maximum | 2 | Floating point | The maximum permitted value. | %
| YES | Input Register | 12286 | r_HD_PID_RawLoopOutput.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| YES | Discrete Input | 12290 | b_HD_PID_SteadyState.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Discrete Input | 12291 | b_HD_PID_SteadyState.Value | 1 | Bool | This is the value shown on the touchscreen for flag indicating if the unit is operating under smooth, steady-state temperature regulation. 0=pid not in steady-state operation; 1=pid in steady-state operation. | Off/On
| YES | Input Register | 12290 | b_HD_PID_SteadyState.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| NO | Discrete Input | 12300 | n_HD_AT_State.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12300 | n_HD_AT_State.Value | 2 | Integer | Not currently implemented. | %
| NO | Input Register | 12302 | n_HD_AT_State.Minimum | 2 | Integer | Not currently implemented. | %
| NO | Input Register | 12304 | n_HD_AT_State.Maximum | 2 | Integer | Not currently implemented. | %
| NO | Input Register | 12306 | n_HD_AT_State.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 12310 | r_HD_AT_Output.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12310 | r_HD_AT_Output.Value | 2 | Floating point | Not currently implemented. | %
| NO | Input Register | 12312 | r_HD_AT_Output.Minimum | 2 | Floating point | Not currently implemented. | %
| NO | Input Register | 12314 | r_HD_AT_Output.Maximum | 2 | Floating point | Not currently implemented. | %
| NO | Input Register | 12316 | r_HD_AT_Output.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 12320 | r_HD_AT_NewP_Band.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12320 | r_HD_AT_NewP_Band.Value | 2 | Floating point | Not currently implemented. | Δ°C
| NO | Input Register | 12322 | r_HD_AT_NewP_Band.Minimum | 2 | Floating point | Not currently implemented. | Δ°C
| NO | Input Register | 12324 | r_HD_AT_NewP_Band.Maximum | 2 | Floating point | Not currently implemented. | Δ°C
| NO | Input Register | 12326 | r_HD_AT_NewP_Band.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 12330 | r_HD_AT_NewIntegralGain.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12330 | r_HD_AT_NewIntegralGain.Value | 2 | Floating point | Not currently implemented. | seconds
| NO | Input Register | 12332 | r_HD_AT_NewIntegralGain.Minimum | 2 | Floating point | Not currently implemented. | seconds
| NO | Input Register | 12334 | r_HD_AT_NewIntegralGain.Maximum | 2 | Floating point | Not currently implemented. | seconds
| NO | Input Register | 12336 | r_HD_AT_NewIntegralGain.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 12340 | r_HD_AT_NewDerivativeGain.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12340 | r_HD_AT_NewDerivativeGain.Value | 2 | Floating point | Not currently implemented. | seconds
| NO | Input Register | 12342 | r_HD_AT_NewDerivativeGain.Minimum | 2 | Floating point | Not currently implemented. | seconds
| NO | Input Register | 12344 | r_HD_AT_NewDerivativeGain.Maximum | 2 | Floating point | Not currently implemented. | seconds
| NO | Input Register | 12346 | r_HD_AT_NewDerivativeGain.Error | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Discrete Input | 12350 | n_HD_MSM_State.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12350 | n_HD_MSM_State.Value | 2 | Integer | This is the value shown on the touchscreen for MSM State enumeration. 0="Unknown"; 1="Booting"; 2="Starting"; 3="Preparing to Stop"; 4="Stopped"; 5=Preparing to Vent"; 6="Valve Vent"; 7="Pump/Valve Vent"; 8="Preparing to Run"; 9="Running"; 10="Low Pressure Pause"; 11="Auto Cool Stop"; 12="Mold Purge Active"; 13="User Configuration"; 14="Diagnostics"; 15="Factory Configuration"; 16="Preparing to Alarm"; 17="Alarm-Resettable";18=Alarm-Cycle Power"; 19="Alarm-Overtemperature"; 20="Alarm Resetting"; 21="Rebooting". | <enumeration>
| YES | Input Register | 12352 | n_HD_MSM_State.Minimum | 2 | Integer | The minimum permitted value. | <enumeration>
| YES | Input Register | 12354 | n_HD_MSM_State.Maximum | 2 | Integer | The maximum permitted value. | <enumeration>
| YES | Input Register | 12356 | n_HD_MSM_State.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12360 | n_HD_TSM_State.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12360 | n_HD_TSM_State.Value | 2 | Integer | This is the value shown on the touchscreen for TSM State enumeration. 0=Unknown; 1=Boot; 2=Init; 3=Stop; 4=Vent; 5=SV: No Heat/Cool; 6=SV: Heat; 7=SV: Cool; 8=FV: No Heat/Cool; 9=FV: Heat; 10=FV: Less Cool; 11=FV: Less Cool, Prepare to Open; 12=FV: More Cool; 13=FV: More Cool, Prepare to Close; 14=Mod Valve: No Heat/Cool; 15=MV: Heat; 16=MV: Cool; 17=Emergency Cooling (all valve types). | <enumeration>
| YES | Input Register | 12362 | n_HD_TSM_State.Minimum | 2 | Integer | The minimum permitted value. | <enumeration>
| YES | Input Register | 12364 | n_HD_TSM_State.Maximum | 2 | Integer | The maximum permitted value. | <enumeration>
| YES | Input Register | 12366 | n_HD_TSM_State.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| NO | Discrete Input | 12370 | n_HD_NetworkStatus.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12370 | n_HD_NetworkStatus.Value | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 12372 | n_HD_NetworkStatus.Minimum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 12374 | n_HD_NetworkStatus.Maximum | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 12376 | n_HD_NetworkStatus.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Discrete Input | 12380 | n_HD_ModbusErrorCode.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12380 | n_HD_ModbusErrorCode.Value | 2 | Integer | Not currently implemented. | N/A
| NO | Input Register | 12382 | n_HD_ModbusErrorCode.Minimum | 2 | Integer | Not currently implemented. | N/A
| NO | Input Register | 12384 | n_HD_ModbusErrorCode.Maximum | 2 | Integer | Not currently implemented. | N/A
| NO | Input Register | 12386 | n_HD_ModbusErrorCode.Error | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Discrete Input | 12390 | u_HD_RampSoakStep.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12390 | u_HD_RampSoakStep.Value | 2 | Unsigned Integer | This is the value shown on the touchscreen for Ramp/Soak Step. | step
| YES | Input Register | 12392 | u_HD_RampSoakStep.Minimum | 2 | Unsigned Integer | The minimum permitted value. | step
| YES | Input Register | 12394 | u_HD_RampSoakStep.Maximum | 2 | Unsigned Integer | The maximum permitted value. | step
| YES | Input Register | 12396 | u_HD_RampSoakStep.Error | 2 | Unsigned Integer | Describes if value is valid: 10=No Error; 9=Not relevant in current machine state; 4=Not used; 0=Error. | <enumeration>
| YES | Discrete Input | 12400 | n_HD_InterimSetpointDirection.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12400 | n_HD_InterimSetpointDirection.Value | 2 | Integer | This is the value shown on the touchscreen for Interim Setpoint Direction enumeration. 0=No direction; 1=Up; 2=Down. | <enumeration>
| YES | Input Register | 12402 | n_HD_InterimSetpointDirection.Minimum | 2 | Integer | The minimum permitted value. | <enumeration>
| YES | Input Register | 12404 | n_HD_InterimSetpointDirection.Maximum | 2 | Integer | The maximum permitted value. | <enumeration>
| YES | Input Register | 12406 | n_HD_InterimSetpointDirection.Error | 2 | Integer | Describes if value is valid: 10=No Error; 9=Not relevant in current machine state; 0=Error. | <enumeration>
| YES | Discrete Input | 12410 | b_HD_RampSoakShowTime[1] | 1 | Bool | Step #1: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| YES | Discrete Input | 12411 | b_HD_RampSoakShowTime[2] | 1 | Bool | Step #2: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| YES | Discrete Input | 12412 | b_HD_RampSoakShowTime[3] | 1 | Bool | Step #3: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| YES | Discrete Input | 12413 | b_HD_RampSoakShowTime[4] | 1 | Bool | Step #4: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| YES | Discrete Input | 12414 | b_HD_RampSoakShowTime[5] | 1 | Bool | Step #5: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| YES | Discrete Input | 12420 | b_HD_RampSoakShowNextStep[1] | 1 | Bool | Step #1: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| YES | Discrete Input | 12421 | b_HD_RampSoakShowNextStep[2] | 1 | Bool | Step #2: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| YES | Discrete Input | 12422 | b_HD_RampSoakShowNextStep[3] | 1 | Bool | Step #3: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| YES | Discrete Input | 12423 | b_HD_RampSoakShowNextStep[4] | 1 | Bool | Step #4: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| YES | Discrete Input | 12424 | b_HD_RampSoakShowNextStep[5] | 1 | Bool | Step #5: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| YES | Discrete Input | 12430 | u_HD_Countdown.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12430 | u_HD_Countdown.Value | 2 | Unsigned Integer | This is the value shown on the touchscreen for countdown clock. In units of seconds. | seconds
| YES | Input Register | 12432 | u_HD_Countdown.Minimum | 2 | Unsigned Integer | The minimum permitted value. | seconds
| YES | Input Register | 12434 | u_HD_Countdown.Maximum | 2 | Unsigned Integer | The maximum permitted value. | seconds
| YES | Input Register | 12436 | u_HD_Countdown.Error | 2 | Unsigned Integer | Describes if value is valid: 10=No Error; 9=Not relevant in current machine state; 0=Error. | <enumeration>
| YES | Discrete Input | 12440 | u_HD_CountdownType.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12440 | u_HD_CountdownType.Value | 2 | Unsigned Integer | This is the value shown on the touchscreen for countdown event type enumeration. 0=None; 1=Valve Vent; 2=Valve/Pump Vent; 3=Low-Pressure Ride-Through; 4=Low-Pressure Resume; 5=Mold Purge; 6=Ramp/Soak Event; 7=Auto Cool Stop; 8=Reboot; 9=Auto-Restart; 10=Mod Valve Homing; | <enumeration>
| YES | Input Register | 12442 | u_HD_CountdownType.Minimum | 2 | Unsigned Integer | The minimum permitted value. | <enumeration>
| YES | Input Register | 12444 | u_HD_CountdownType.Maximum | 2 | Unsigned Integer | The maximum permitted value. | <enumeration>
| YES | Input Register | 12446 | u_HD_CountdownType.Error | 2 | Unsigned Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12450 | n_HD_RebootMessage.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12450 | n_HD_RebootMessage.Value | 2 | Integer | This is the value shown on the touchscreen for reboot message enumeration. 0="Preparing to Reboot"; 1="Loading Operator Defaults"; 2="Loading Maintenance Defaults"; 3="Changing Units"; 4="Changing Branding"; 5="Changing IO Setup"; 6="Updating Network". | <enumeration>
| YES | Input Register | 12452 | n_HD_RebootMessage.Minimum | 2 | Integer | For details, see Modbus_Status sheet. | <enumeration>
| YES | Input Register | 12454 | n_HD_RebootMessage.Maximum | 2 | Integer | For details, see Modbus_Status sheet. | <enumeration>
| YES | Input Register | 12456 | n_HD_RebootMessage.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12460 | n_HD_Alarm.Implemented | 1 | Bool | Highest Priority Alarm | Off/On
| YES | Input Register | 12460 | n_HD_Alarm.Value | 2 | Integer | Highest Priority Alarm. 1=IO Connection Failure; 2=IO Module Link Failure; 3=IO Module Hardware Mismatch; 4=IO Module Internal Fault; 5=IO Point Failure; 6=Power Supply Voltage Low; 7=Logic Supply Voltage Low; 8=Overtemperature Fault; 9=Heater Contactor Stuck Closed; 10=Temperature Over Limit; 11=Unbranded; 12=Factory Options Not Set; 13=Electric Power Fault; 14=Pump Contactor Stuck Closed; 15=Heater Contactor Stuck Open; 16=Pump Contactor Stuck Open; 17=System Pressure Too High; 18=Electrical Panel Too Hot; 19=Temperature Under Limit; 20=Brownout Occurred; 21=Temperature Over Setting; 22=Temperature Under Setting; 23=Low Pressure Shutdown; 24=Low Pressure Too Many Events; 25=Pump Overload Tripped; 26=Flowmeter Low Flow; 27=To Proc RTD Probe Open; 28=To Proc RTD Probe Short; 29=To Proc RTD Probe Error; 30=From Proc RTD Probe Open; 31=From Proc RTD Probe Short; 32=From Proc RTD Probe Error; 33=Remote RTD Probe Open; 34=Remote RTD Probe Short; 35=Remote RTD Probe Error; 36=Analog Process In Too High; 37=Analog Process In Too Low; 38=Analog Process In Error; 39=Network Process In Too High; 40=Network Process In Too Low; 41=Network Proc In Heartbeat Lost; 42=Analog Setpoint Too High; 43=Analog Setpoint Too Low; 44=Analog Setpoint Error; 45=Network Setpoint High; 46=Network Setpoint Low; 47=Network Setpoint Heartbeat Lost; 48=Pressure Below Minimum; 49=Need More Press for this Temp; 50=From Process Press Sensor High; 51=From Process Press Sensor Low; 52=From Process Press Sensor Error; 53=To Process Press Sensor High; 54=To Process Press Sensor Low; 55=To Process Press Sensor Error; 56=Flowmeter Signal Too High; 57=Flowmeter Signal Too Low; 58=Flowmeter Signal Error; 59=Temperature Deviation High; 60=Temperature Deviation Low; 61=Network Heartbeat Lost; 62=Ramp/Soak Interrupted; 63=Autotune Startg Output Too High; 64=Autotune Process Response Slow; 65=Autotune Time Const Not Found; 66=Autotune Process Limit Exceeded. | <enumeration>
| YES | Input Register | 12462 | n_HD_Alarm.Minimum | 2 | Integer | Highest Priority Alarm | <enumeration>
| YES | Input Register | 12464 | n_HD_Alarm.Maximum | 2 | Integer | Highest Priority Alarm | <enumeration>
| YES | Input Register | 12466 | n_HD_Alarm.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12470 | n_HD_Warning.Implemented | 1 | Bool | Highest Priority Warning | Off/On
| YES | Input Register | 12470 | n_HD_Warning.Value | 2 | Integer | Highest Priority Warning. 1=Pump Overload Tripped; 2=Flowmeter Bad Flow; 3=To Proc RTD Probe Open (f/o); 4=To Proc RTD Probe Short (f/o); 5=To Proc RTD Probe Error (f/o); 6=From Proc RTD Probe Open (f/o); 7=From Proc RTD Probe Short (f/o); 8=From Proc RTD Probe Error (f/o); 9=Remote RTD Probe Open (f/o); 10=Remote RTD Probe Short (f/o); 11=Remote RTD Probe Error (f/o); 12=Analog Process In Too High (f/o); 13=Analog Process In Too Low (f/o); 14=Analog Process In Error (f/o); 15=Network Proc In Too High (f/o); 16=Network Proc In Too Low (f/o); 17=Network Proc In HB Lost (f/o); 18=Analog Setpoint Too High (f/o); 19=Analog Setpoint Too Low (f/o); 20=Analog Setpoint Error (f/o); 21=Network Setpoint Too High (f/o); 22=Network Setpoint Too Low (f/o); 23=Network Setpoint HB Lost (f/o); 24=Pressure Below Minimum; 25=Need More Press for this Temp; 26=Setpoint Too High for Pressure; 27=To Proc Pressure Sensor High; 28=To Proc Pressure Sensor Low; 29=To Proc Pressure Sensor Error; 30=To Proc RTD Probe Open; 31=To Proc RTD Probe Short; 32=To Proc RTD Probe Error; 33=From Proc RTD Probe Open; 34=From Proc RTD Probe Short; 35=From Proc RTD Probe Error; 36=Flowmeter Signal Too High; 37=Flowmeter Signal Too Low; 38=Flowmeter Signal Error; 39=Flash Memory Error; 40=Temperature Deviation High; 41=Temperature Deviation Low; 42=Network Heartbeat Lost; 43=Too Frequent Heat Cycles; 44=Work Out Heater Contactor; 45=Clock Not Set. | <enumeration>
| YES | Input Register | 12472 | n_HD_Warning.Minimum | 2 | Integer | Highest Priority Warning | <enumeration>
| YES | Input Register | 12474 | n_HD_Warning.Maximum | 2 | Integer | Highest Priority Warning | <enumeration>
| YES | Input Register | 12476 | n_HD_Warning.Error | 2 | Integer | Highest Priority Warning | <enumeration>
| YES | Discrete Input | 12480 | b_HD_AlarmSilenceActive.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Discrete Input | 12481 | b_HD_AlarmSilenceActive.Value | 1 | Bool | This is the value shown on the touchscreen for high if the there is an alarm, but it has been silenced. 0=alarm not silenced; 1=alarm silenced. | Off/On
| YES | Input Register | 12480 | b_HD_AlarmSilenceActive.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12490 | r_HD_NPSHa.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12490 | r_HD_NPSHa.Value | 2 | Floating point | This is the value shown on the touchscreen for net positive suction head available for pump. In units of psi. | psi
| YES | Input Register | 12492 | r_HD_NPSHa.Minimum | 2 | Floating point | The minimum permitted value. | psi
| YES | Input Register | 12494 | r_HD_NPSHa.Maximum | 2 | Floating point | The maximum permitted value. | psi
| YES | Input Register | 12496 | r_HD_NPSHa.Error | 2 | Integer | Describes if value is valid: 10=No Error; 3=Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12500 | r_HD_NPSHr.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12500 | r_HD_NPSHr.Value | 2 | Floating point | This is the value shown on the touchscreen for net positive suction head required by pump. In units of psi. | psi
| YES | Input Register | 12502 | r_HD_NPSHr.Minimum | 2 | Floating point | The minimum permitted value. | psi
| YES | Input Register | 12504 | r_HD_NPSHr.Maximum | 2 | Floating point | The maximum permitted value. | psi
| YES | Input Register | 12506 | r_HD_NPSHr.Error | 2 | Integer | Describes if value is valid: 10=No Error; 3=Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12510 | r_HD_SystemPower_kW.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12510 | r_HD_SystemPower_kW.Value | 2 | Floating point | This is the value shown on the touchscreen for current electrical power being consumed by the unit (according to component nameplate ratings). In units of kW. | kW
| YES | Input Register | 12512 | r_HD_SystemPower_kW.Minimum | 2 | Floating point | The minimum permitted value. | kW
| YES | Input Register | 12514 | r_HD_SystemPower_kW.Maximum | 2 | Floating point | The maximum permitted value. | kW
| YES | Input Register | 12516 | r_HD_SystemPower_kW.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12520 | r_HD_SystemNominalPower_kW.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12520 | r_HD_SystemNominalPower_kW.Value | 2 | Floating point | This is the value shown on the touchscreen for nominal electrical power being consumed by the unit if it was fully operational and heater was operating at 100%. In units of kW. | kW
| YES | Input Register | 12522 | r_HD_SystemNominalPower_kW.Minimum | 2 | Floating point | The minimum permitted value. | kW
| YES | Input Register | 12524 | r_HD_SystemNominalPower_kW.Maximum | 2 | Floating point | The maximum permitted value. | kW
| YES | Input Register | 12526 | r_HD_SystemNominalPower_kW.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12530 | s_HD_OS_Version.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12530 | s_HD_OS_Version.Value | 8 | String | This is the value shown on the touchscreen for firmware/os software revision level. | N/A
| YES | Input Register | 12538 | s_HD_OS_Version.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12540 | r_HD_SoftwareVersion.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12540 | r_HD_SoftwareVersion.Value | 2 | Floating point | This is the value shown on the touchscreen for application software revision level. | N/A
| YES | Input Register | 12542 | r_HD_SoftwareVersion.Minimum | 2 | Floating point | The minimum permitted value. | N/A
| YES | Input Register | 12544 | r_HD_SoftwareVersion.Maximum | 2 | Floating point | The maximum permitted value. | N/A
| YES | Input Register | 12546 | r_HD_SoftwareVersion.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12550 | u_HD_HEALTH_HeaterContactorOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12550 | u_HD_HEALTH_HeaterContactorOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the electromechanical heater contactor. In units of operations. | operations
| YES | Input Register | 12552 | u_HD_HEALTH_HeaterContactorOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12554 | u_HD_HEALTH_HeaterContactorOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12556 | u_HD_HEALTH_HeaterContactorOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12558 | u_NET_HEALTH_HeaterContrOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the electromechanical heater contactor. In units of operations. | operations
| YES | Discrete Input | 12560 | u_HD_HEALTH_HeaterContactorRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12560 | u_HD_HEALTH_HeaterContactorRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the electromechanical heater contactor. In units of hours. | hours
| YES | Input Register | 12562 | u_HD_HEALTH_HeaterContactorRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12564 | u_HD_HEALTH_HeaterContactorRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12566 | u_HD_HEALTH_HeaterContactorRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12568 | u_NET_HEALTH_HeaterContrRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the electromechanical heater contactor. In units of hours. | hours
| YES | Discrete Input | 12570 | u_HD_HEALTH_HeaterContrOpenDly.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12570 | u_HD_HEALTH_HeaterContrOpenDly.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for time delay between turning off the coil power to the heater electromechanical contactor & sensing the opening of the armature via the aux contacts on the heater electromechanical contactor. In units of milliseconds. | milliseconds
| YES | Input Register | 12572 | u_HD_HEALTH_HeaterContrOpenDly.Minimum | 2 | Unsigned integer | The minimum permitted value. | milliseconds
| YES | Input Register | 12574 | u_HD_HEALTH_HeaterContrOpenDly.Maximum | 2 | Unsigned integer | The maximum permitted value. | milliseconds
| YES | Input Register | 12576 | u_HD_HEALTH_HeaterContrOpenDly.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12578 | u_HD_HEALTH_HeaterContrCloseDly.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12578 | u_HD_HEALTH_HeaterContrCloseDly.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for time delay between turning on the coil power to the heater electromechanical contactor & sensing the closing of the armature via the aux contacts on the heater electromechanical contactor. In units of milliseconds. | milliseconds
| YES | Input Register | 12580 | u_HD_HEALTH_HeaterContrCloseDly.Minimum | 2 | Unsigned integer | The minimum permitted value. | milliseconds
| YES | Input Register | 12582 | u_HD_HEALTH_HeaterContrCloseDly.Maximum | 2 | Unsigned integer | The maximum permitted value. | milliseconds
| YES | Input Register | 12584 | u_HD_HEALTH_HeaterContrCloseDly.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12588 | u_HD_HEALTH_HeaterSSR_Ops.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12588 | u_HD_HEALTH_HeaterSSR_Ops.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the solid state heater contactor. In units of operations. | operations
| YES | Input Register | 12590 | u_HD_HEALTH_HeaterSSR_Ops.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12592 | u_HD_HEALTH_HeaterSSR_Ops.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12594 | u_HD_HEALTH_HeaterSSR_Ops.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12596 | u_NET_HEALTH_HeaterSSR_Ops_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the solid state heater contactor. In units of operations. | operations
| YES | Discrete Input | 12598 | u_HD_HEALTH_HeaterSSR_Rt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12598 | u_HD_HEALTH_HeaterSSR_Rt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the solid state heater contactor. In units of hours. | hours
| YES | Input Register | 12600 | u_HD_HEALTH_HeaterSSR_Rt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12602 | u_HD_HEALTH_HeaterSSR_Rt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12604 | u_HD_HEALTH_HeaterSSR_Rt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12606 | u_NET_HEALTH_HeaterSSR_Rt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the solid state heater contactor. In units of hours. | hours
| YES | Discrete Input | 12608 | u_HD_HEALTH_HeaterOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12608 | u_HD_HEALTH_HeaterOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the heater. In units of operations. | operations
| YES | Input Register | 12610 | u_HD_HEALTH_HeaterOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12612 | u_HD_HEALTH_HeaterOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12614 | u_HD_HEALTH_HeaterOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12616 | u_NET_HEALTH_HeaterOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the heater. In units of operations. | operations
| YES | Discrete Input | 12618 | u_HD_HEALTH_HeaterRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12618 | u_HD_HEALTH_HeaterRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the heater. In units of hours. | hours
| YES | Input Register | 12620 | u_HD_HEALTH_HeaterRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12622 | u_HD_HEALTH_HeaterRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12624 | u_HD_HEALTH_HeaterRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12626 | u_NET_HEALTH_HeaterRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the heater. In units of hours. | hours
| YES | Discrete Input | 12628 | u_HD_HEALTH_CV_ActuationRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12628 | u_HD_HEALTH_CV_ActuationRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the cooling valve. In units of hours. | hours
| YES | Input Register | 12630 | u_HD_HEALTH_CV_ActuationRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12632 | u_HD_HEALTH_CV_ActuationRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12634 | u_HD_HEALTH_CV_ActuationRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12636 | u_NET_HEALTH_CV_ActuationRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the cooling valve. In units of hours. | hours
| YES | Discrete Input | 12638 | u_HD_HEALTH_CV_OpenOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12638 | u_HD_HEALTH_CV_OpenOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the cooling valve solenoid or floating valve open direction. In units of operations. | operations
| YES | Input Register | 12640 | u_HD_HEALTH_CV_OpenOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12642 | u_HD_HEALTH_CV_OpenOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12644 | u_HD_HEALTH_CV_OpenOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12646 | u_NET_HEALTH_CV_OpenOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the cooling valve solenoid or floating valve open direction. In units of operations. | operations
| YES | Discrete Input | 12648 | u_HD_HEALTH_CV_OpenRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12648 | u_HD_HEALTH_CV_OpenRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the cooling valve solenoid or floating valve open direction. In units of hours. | hours
| YES | Input Register | 12650 | u_HD_HEALTH_CV_OpenRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12652 | u_HD_HEALTH_CV_OpenRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12654 | u_HD_HEALTH_CV_OpenRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12656 | u_NET_HEALTH_CV_OpenRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the cooling valve solenoid or floating valve open direction. In units of hours. | hours
| YES | Discrete Input | 12658 | u_HD_HEALTH_CV_CloseOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12658 | u_HD_HEALTH_CV_CloseOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the floating valve close direction. In units of operations. | operations
| YES | Input Register | 12660 | u_HD_HEALTH_CV_CloseOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12662 | u_HD_HEALTH_CV_CloseOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12664 | u_HD_HEALTH_CV_CloseOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12666 | u_NET_HEALTH_CV_CloseOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the floating valve close direction. In units of operations. | operations
| YES | Discrete Input | 12668 | u_HD_HEALTH_CV_CloseRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12668 | u_HD_HEALTH_CV_CloseRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the floating valve close direction. In units of hours. | hours
| YES | Input Register | 12670 | u_HD_HEALTH_CV_CloseRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12672 | u_HD_HEALTH_CV_CloseRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12674 | u_HD_HEALTH_CV_CloseRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12676 | u_NET_HEALTH_CV_CloseRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the floating valve close direction. In units of hours. | hours
| YES | Discrete Input | 12678 | u_HD_HEALTH_PumpOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12678 | u_HD_HEALTH_PumpOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the pump. In units of operations. | operations
| YES | Input Register | 12680 | u_HD_HEALTH_PumpOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12682 | u_HD_HEALTH_PumpOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12684 | u_HD_HEALTH_PumpOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12686 | u_NET_HEALTH_PumpOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the pump. In units of operations. | operations
| YES | Discrete Input | 12688 | u_HD_HEALTH_PumpRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12688 | u_HD_HEALTH_PumpRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the pump. In units of hours. | hours
| YES | Input Register | 12690 | u_HD_HEALTH_PumpRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12692 | u_HD_HEALTH_PumpRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12694 | u_HD_HEALTH_PumpRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12696 | u_NET_HEALTH_PumpRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the pump. In units of hours. | hours
| YES | Discrete Input | 12698 | u_HD_HEALTH_PumpContactorOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12698 | u_HD_HEALTH_PumpContactorOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the pump contactor. In units of operations. | operations
| YES | Input Register | 12700 | u_HD_HEALTH_PumpContactorOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12702 | u_HD_HEALTH_PumpContactorOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12704 | u_HD_HEALTH_PumpContactorOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12706 | u_NET_HEALTH_PumpContactorOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the pump contactor. In units of operations. | operations
| YES | Discrete Input | 12708 | u_HD_HEALTH_PumpContactorRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12708 | u_HD_HEALTH_PumpContactorRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the pump contactor. In units of hours. | hours
| YES | Input Register | 12710 | u_HD_HEALTH_PumpContactorRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12712 | u_HD_HEALTH_PumpContactorRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12714 | u_HD_HEALTH_PumpContactorRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12716 | u_NET_HEALTH_PumpContactorRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the pump contactor. In units of hours. | hours
| YES | Discrete Input | 12718 | u_HD_HEALTH_PumpContrOpenDly.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12718 | u_HD_HEALTH_PumpContrOpenDly.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for time delay between turning off the coil power to the pump electromechanical contactor & sensing the opening of the armature via the aux contacts on the pump electromechanical contactor. In units of milliseconds. | milliseconds
| YES | Input Register | 12720 | u_HD_HEALTH_PumpContrOpenDly.Minimum | 2 | Unsigned integer | The minimum permitted value. | milliseconds
| YES | Input Register | 12722 | u_HD_HEALTH_PumpContrOpenDly.Maximum | 2 | Unsigned integer | The maximum permitted value. | milliseconds
| YES | Input Register | 12724 | u_HD_HEALTH_PumpContrOpenDly.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12726 | u_HD_HEALTH_PumpContrCloseDly.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12726 | u_HD_HEALTH_PumpContrCloseDly.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for time delay between turning on the coil power on the pump electromechanical contactor & sensing the closing of the armature via the aux contacts on the pump electromechanical contactor. In units of milliseconds. | milliseconds
| YES | Input Register | 12728 | u_HD_HEALTH_PumpContrCloseDly.Minimum | 2 | Unsigned integer | The minimum permitted value. | milliseconds
| YES | Input Register | 12730 | u_HD_HEALTH_PumpContrCloseDly.Maximum | 2 | Unsigned integer | The maximum permitted value. | milliseconds
| YES | Input Register | 12732 | u_HD_HEALTH_PumpContrCloseDly.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12736 | u_HD_HEALTH_PresSwOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12736 | u_HD_HEALTH_PresSwOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the pressure switch. In units of operations. | operations
| YES | Input Register | 12738 | u_HD_HEALTH_PresSwOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12740 | u_HD_HEALTH_PresSwOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12742 | u_HD_HEALTH_PresSwOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12744 | u_NET_HEALTH_PresSwOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the pressure switch. In units of operations. | operations
| YES | Discrete Input | 12746 | u_HD_HEALTH_MoldPurgeOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12746 | u_HD_HEALTH_MoldPurgeOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the mold purge solenoid valves. In units of operations. | operations
| YES | Input Register | 12748 | u_HD_HEALTH_MoldPurgeOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12750 | u_HD_HEALTH_MoldPurgeOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12752 | u_HD_HEALTH_MoldPurgeOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12754 | u_NET_HEALTH_MoldPurgeOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the mold purge solenoid valves. In units of operations. | operations
| YES | Discrete Input | 12756 | u_HD_HEALTH_VentSolOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12756 | u_HD_HEALTH_VentSolOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the vent solenoid. (not shown in HMI.) In unit of operations. | operations
| YES | Input Register | 12758 | u_HD_HEALTH_VentSolOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12760 | u_HD_HEALTH_VentSolOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12762 | u_HD_HEALTH_VentSolOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12764 | u_NET_HEALTH_VentSolOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the vent solenoid. (not shown in HMI.) In unit of operations. | operations
| YES | Discrete Input | 12766 | u_HD_HEALTH_PumpOL_Ops.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12766 | u_HD_HEALTH_PumpOL_Ops.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for count of number of trips of the pump overload. In units of operations. | operations
| YES | Input Register | 12768 | u_HD_HEALTH_PumpOL_Ops.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12770 | u_HD_HEALTH_PumpOL_Ops.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12772 | u_HD_HEALTH_PumpOL_Ops.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12774 | u_NET_HEALTH_PumpOL_Ops_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable count of number of trips of the pump overload. In units of operations. | operations
| YES | Discrete Input | 12776 | u_HD_HEALTH_AlarmOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12776 | u_HD_HEALTH_AlarmOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for count for number of alarms. In units of operations. | operations
| YES | Input Register | 12778 | u_HD_HEALTH_AlarmOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12780 | u_HD_HEALTH_AlarmOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12782 | u_HD_HEALTH_AlarmOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12784 | u_NET_HEALTH_AlarmOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable count for number of alarms. In units of operations. | operations
| YES | Discrete Input | 12786 | u_HD_HEALTH_HighTempOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12786 | u_HD_HEALTH_HighTempOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for count for number of high-temperature alarms. In units of operations. | operations
| YES | Input Register | 12788 | u_HD_HEALTH_HighTempOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12790 | u_HD_HEALTH_HighTempOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12792 | u_HD_HEALTH_HighTempOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12794 | u_NET_HEALTH_HighTempOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable count for number of high-temperature alarms. In units of operations. | operations
| YES | Discrete Input | 12796 | u_HD_HEALTH_PhaseMonitorOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12796 | u_HD_HEALTH_PhaseMonitorOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for count for number of phase monitor alarms. In units of operations. | operations
| YES | Input Register | 12798 | u_HD_HEALTH_PhaseMonitorOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12800 | u_HD_HEALTH_PhaseMonitorOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12802 | u_HD_HEALTH_PhaseMonitorOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12804 | u_NET_HEALTH_PhaseMonitorOps_NR | 2 | Integer | This is the value shown on the touchscreen for non-resettable count for number of phase monitor alarms. In units of operations. | operations
| YES | Discrete Input | 12806 | u_HD_HEALTH_CoolingLTA.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12806 | u_HD_HEALTH_CoolingLTA.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for long term cooling capacity utilization. In units of %. | %
| YES | Input Register | 12808 | u_HD_HEALTH_CoolingLTA.Minimum | 2 | Unsigned integer | The minimum permitted value. | %
| YES | Input Register | 12810 | u_HD_HEALTH_CoolingLTA.Maximum | 2 | Unsigned integer | The maximum permitted value. | %
| YES | Input Register | 12812 | u_HD_HEALTH_CoolingLTA.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12816 | u_HD_HEALTH_HeatingLTA.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12816 | u_HD_HEALTH_HeatingLTA.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for long term heating capacity utilization. In units of %. | %
| YES | Input Register | 12818 | u_HD_HEALTH_HeatingLTA.Minimum | 2 | Unsigned integer | The minimum permitted value. | %
| YES | Input Register | 12820 | u_HD_HEALTH_HeatingLTA.Maximum | 2 | Unsigned integer | The maximum permitted value. | %
| YES | Input Register | 12822 | u_HD_HEALTH_HeatingLTA.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12826 | u_HD_HEALTH_LastAlarmDuration.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12826 | u_HD_HEALTH_LastAlarmDuration.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for last alarm duration. In units of seconds. | seconds
| YES | Input Register | 12828 | u_HD_HEALTH_LastAlarmDuration.Minimum | 2 | Unsigned integer | The minimum permitted value. | seconds
| YES | Input Register | 12830 | u_HD_HEALTH_LastAlarmDuration.Maximum | 2 | Unsigned integer | The maximum permitted value. | seconds
| YES | Input Register | 12832 | u_HD_HEALTH_LastAlarmDuration.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12836 | u_HD_HEALTH_LowPressure.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12836 | u_HD_HEALTH_LowPressure.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for count of low pressure pause states. | operations
| YES | Input Register | 12838 | u_HD_HEALTH_LowPressure.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12840 | u_HD_HEALTH_LowPressure.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12842 | u_HD_HEALTH_LowPressure.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12844 | u_NET_HEALTH_LowPressure_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for count of low pressure pause states. | operations
| NO | Discrete Input | 12846 | u_HD_HEALTH_MemWrites_x100000.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12846 | u_HD_HEALTH_MemWrites_x100000.Value | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12848 | u_HD_HEALTH_MemWrites_x100000.Minimum | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12850 | u_HD_HEALTH_MemWrites_x100000.Maximum | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12852 | u_HD_HEALTH_MemWrites_x100000.Error | 2 | Integer | Not currently implemented. | <enumeration>
| YES | Discrete Input | 12856 | u_HD_HEALTH_LoopTime_ms.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12856 | u_HD_HEALTH_LoopTime_ms.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for last logic execution loop time. In units of milliseconds. | milliseconds
| YES | Input Register | 12858 | u_HD_HEALTH_LoopTime_ms.Minimum | 2 | Unsigned integer | The minimum permitted value. | milliseconds
| YES | Input Register | 12860 | u_HD_HEALTH_LoopTime_ms.Maximum | 2 | Unsigned integer | The maximum permitted value. | milliseconds
| YES | Input Register | 12862 | u_HD_HEALTH_LoopTime_ms.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12866 | u_HD_HEALTH_LoopTimeMax.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12866 | u_HD_HEALTH_LoopTimeMax.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for maximum logic execution loop time. In units of milliseconds. | milliseconds
| YES | Input Register | 12868 | u_HD_HEALTH_LoopTimeMax.Minimum | 2 | Unsigned integer | The minimum permitted value. | milliseconds
| YES | Input Register | 12870 | u_HD_HEALTH_LoopTimeMax.Maximum | 2 | Unsigned integer | The maximum permitted value. | milliseconds
| YES | Input Register | 12872 | u_HD_HEALTH_LoopTimeMax.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Discrete Input | 12876 | u_HD_HEALTH_FlowswitchOps.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12876 | u_HD_HEALTH_FlowswitchOps.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational cycle count for the flow switch. In units of operations. | operations
| YES | Input Register | 12878 | u_HD_HEALTH_FlowswitchOps.Minimum | 2 | Unsigned integer | The minimum permitted value. | operations
| YES | Input Register | 12880 | u_HD_HEALTH_FlowswitchOps.Maximum | 2 | Unsigned integer | The maximum permitted value. | operations
| YES | Input Register | 12882 | u_HD_HEALTH_FlowswitchOps.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12884 | u_NET_HEALTH_FlowswitchOps_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational cycle count for the flow switch. In units of operations. | operations
| YES | Discrete Input | 12886 | u_HD_HEALTH_FlowswitchRt.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12886 | u_HD_HEALTH_FlowswitchRt.Value | 2 | Unsigned integer | This is the value shown on the touchscreen for operational run time for the flow switch. In units of hours. | hours
| YES | Input Register | 12888 | u_HD_HEALTH_FlowswitchRt.Minimum | 2 | Unsigned integer | The minimum permitted value. | hours
| YES | Input Register | 12890 | u_HD_HEALTH_FlowswitchRt.Maximum | 2 | Unsigned integer | The maximum permitted value. | hours
| YES | Input Register | 12892 | u_HD_HEALTH_FlowswitchRt.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| YES | Input Register | 12894 | u_NET_HEALTH_FlowswitchRt_NR | 2 | Unsigned integer | This is the value shown on the touchscreen for non-resettable operational run time for the flow switch. In units of hours. | hours
| NO | Discrete Input | 12896 | u_HD_HEALTH_CrashCoolOps.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12896 | u_HD_HEALTH_CrashCoolOps.Value | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12898 | u_HD_HEALTH_CrashCoolOps.Minimum | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12900 | u_HD_HEALTH_CrashCoolOps.Maximum | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12902 | u_HD_HEALTH_CrashCoolOps.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 12904 | u_NET_HEALTH_CrashCoolOps_NR | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Discrete Input | 12906 | u_HD_HEALTH_CrashCoolRt.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12906 | u_HD_HEALTH_CrashCoolRt.Value | 2 | Unsigned integer | Not currently implemented. | hours
| NO | Input Register | 12908 | u_HD_HEALTH_CrashCoolRt.Minimum | 2 | Unsigned integer | Not currently implemented. | hours
| NO | Input Register | 12910 | u_HD_HEALTH_CrashCoolRt.Maximum | 2 | Unsigned integer | Not currently implemented. | hours
| NO | Input Register | 12912 | u_HD_HEALTH_CrashCoolRt.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 12914 | u_NET_HEALTH_CrashCoolRt_NR | 2 | Unsigned integer | Not currently implemented. | hours
| NO | Discrete Input | 12916 | u_HD_HEALTH_CCSS_FillValveOps.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12916 | u_HD_HEALTH_CCSS_FillValveOps.Value | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12918 | u_HD_HEALTH_CCSS_FillValveOps.Minimum | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12920 | u_HD_HEALTH_CCSS_FillValveOps.Maximum | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Input Register | 12922 | u_HD_HEALTH_CCSS_FillValveOps.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 12924 | u_NET_HEALTH_CCSS_FillVlvOps_NR | 2 | Unsigned integer | Not currently implemented. | operations
| NO | Discrete Input | 12926 | u_HD_HEALTH_CCSS_FillValveRt.Implemented | 1 | Bool | Not currently implemented. | Off/On
| NO | Input Register | 12926 | u_HD_HEALTH_CCSS_FillValveRt.Value | 2 | Unsigned integer | Not currently implemented. | hours
| NO | Input Register | 12928 | u_HD_HEALTH_CCSS_FillValveRt.Minimum | 2 | Unsigned integer | Not currently implemented. | hours
| NO | Input Register | 12930 | u_HD_HEALTH_CCSS_FillValveRt.Maximum | 2 | Unsigned integer | Not currently implemented. | hours
| NO | Input Register | 12932 | u_HD_HEALTH_CCSS_FillValveRt.Error | 2 | Integer | Not currently implemented. | <enumeration>
| NO | Input Register | 12934 | u_NET_HEALTH_CCSS_FillVlvRt_NR | 2 | Unsigned integer | Not currently implemented. | hours
| YES | Discrete Input | 12936 | r_HD_HEALTH_ElecEnclosureTemp.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| YES | Input Register | 12936 | r_HD_HEALTH_ElecEnclosureTemp.Value | 2 | Floating point | This is the value shown on the touchscreen for temperature of the electrical enclosure. In units of °C. | °C
| YES | Input Register | 12938 | r_HD_HEALTH_ElecEnclosureTemp.Minimum | 2 | Floating point | The minimum permitted value. | °C
| YES | Input Register | 12940 | r_HD_HEALTH_ElecEnclosureTemp.Maximum | 2 | Floating point | The maximum permitted value. | °C
| YES | Input Register | 12942 | r_HD_HEALTH_ElecEnclosureTemp.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| NO | Discrete Input | 12946 | n_HD_ScreensaverColor.Implemented | 1 | Bool | This value is only valid on the unit if this bit is TRUE. | Off/On
| NO | Input Register | 12946 | n_HD_ScreensaverColor.Value | 2 | Integer | The color of the screensaver. 0=Unknown; 1=Stopped (Black background, white text); 2=Running (Green background, white text); 3=Non-Shutdown Alarm (Warning) (Orange background, black text); 4=Shutdown Alarm (Red background, black text) | <enumeration>
| NO | Input Register | 12948 | n_HD_ScreensaverColor.Minimum | 2 | Integer | The minimum permitted value. | <enumeration>
| NO | Input Register | 12950 | n_HD_ScreensaverColor.Maximum | 2 | Integer | The maximum permitted value. | <enumeration>
| NO | Input Register | 12952 | n_HD_ScreensaverColor.Error | 2 | Integer | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
Power Consumption, intended for individual read only as necessary.
| YES | Input Register | 14000 | r_PumpNominalPower_W | 2 | Floating point | The electrical nameplate power the pump will consume, when running. In units of watts (W). | W
| YES | Input Register | 14002 | r_HeaterNominalPower_W | 2 | Floating point | The electrical nameplate power the heater will consume, when running at 100%. In units of watts (W). | W
| YES | Input Register | 14004 | r_ControlNominalPower_W | 2 | Floating point | The electrical power the internal controls will consume. In units of watts (W). | W
| YES | Input Register | 14006 | r_SystemNominalPower_kW | 2 | Floating point | The total electrical nameplate power the unit will consume when fully operational and heating at 100%. In units of kilowatts (kW). | kW
| YES | Input Register | 14008 | r_PumpPower_W | 2 | Floating point | The electrical power the pump is currently consuming (based on nameplate, if running). In units of watts (W). | W
| YES | Input Register | 14010 | r_HeaterPower_W | 2 | Floating point | The electrical power the heater is currently consuming (based on nameplate if running at 100%. In units of watts (W). | W
| YES | Input Register | 14012 | r_ControlPower_W | 2 | Floating point | The electrical power the internal controls are consuming. In units of watts (W). | W
| YES | Input Register | 14014 | r_SystemPower_kW | 2 | Floating point | The total electrical power the unit is currently consuming (based on nameplate ratings of components). In units of kilowatts (kW). | kW
Date/Time, intended for individual read/write only as necessary.
| YES | Input Register | 15000 | st_CurrentLocalDateTime.Year | 1 | Integer | See details on Modbus_Status sheet. 4-digit year format. | N/A
| YES | Input Register | 15001 | st_CurrentLocalDateTime.Month | 1 | Integer | See details on Modbus_Status sheet. | N/A
| YES | Input Register | 15002 | st_CurrentLocalDateTime.Day | 1 | Integer | See details on Modbus_Status sheet. | N/A
| YES | Input Register | 15003 | st_CurrentLocalDateTime.Hour | 1 | Integer | See details on Modbus_Status sheet. 24-hour format. | N/A
| YES | Input Register | 15004 | st_CurrentLocalDateTime.Minute | 1 | Integer | See details on Modbus_Status sheet. | N/A
| YES | Input Register | 15005 | st_CurrentLocalDateTime.Second | 1 | Integer | See details on Modbus_Status sheet. | N/A
| YES | Input Register | 15006 | st_CurrentLocalDateTime.DayOfWeek | 1 | Integer | See details on Modbus_Status sheet. 1 through 7, 1=Monday. | N/A
| YES | Input Register | 15007 | st_CurrentLocalDateTime.TimezoneOffset | 2 | Floating point | See details on Modbus_Status sheet. | N/A
| YES | Input Register | 15009 | st_CurrentLocalDateTime.MsSincePowerup | 2 | Integer | See details on Modbus_Status sheet. | N/A
| YES | Input Register | 15011 | st_CurrentLocalDateTime.MsSinceBootup | 2 | Integer | See details on Modbus_Status sheet.
| NO | Input Register | 15013 | st_CurrentLocalDateTime.DstActive | 1 | Integer | See details on Modbus_Status sheet. Not currently implemented. | N/A
| NO | Discrete Input | 15000 | st_CurrentLocalDateTime.DstAutoChangeActive | 1 | Bool | See details on Modbus_Status sheet. Not currently implemented.
| YES | Coil | 15000 | st_NET_DateTimeToSet.Execute | 1 | Bool | Set this bit high to load "To Set" times into the real time clock. | N/A
| YES | Holding Register | 15000 | st_NET_DateTimeToSet.Year | 1 | Integer | Time to set. 4-digit year format. | N/A
| YES | Holding Register | 15001 | st_NET_DateTimeToSet.Month | 1 | Integer | Time to set. | N/A
| YES | Holding Register | 15002 | st_NET_DateTimeToSet.Day | 1 | Integer | Time to set. | N/A
| YES | Holding Register | 15003 | st_NET_DateTimeToSet.Hour | 1 | Integer | Time to set. 24-hour format. | N/A
| YES | Holding Register | 15004 | st_NET_DateTimeToSet.Minute | 1 | Integer | Time to set. | N/A
| YES | Holding Register | 15005 | st_NET_DateTimeToSet.Second | 1 | Integer | Time to set. | N/A
| YES | Input Register | 15020 | n_NET_RTC_SetClockCount | 2 | Integer | Number of times the RTC has been set on the unit. | counts
Security, intended for individual read/write only as necessary.
| YES | Input Register | 15500 | gUserLevel | 1 | Integer | Current local authenticated user. | N/A
| NO | Coil | 15500 |  | 1 | Bool | Generate timecode seed. -- Not needed. Timecode seeds are always generated and up-to-date. Disabled.
| YES | Input Register | 15600 | gModbusUser.Timecode[0] | 1 | Integer | Timecode seed #1. | N/A
| YES | Input Register | 15601 | gModbusUser.Timecode[1] | 1 | Integer | Timecode seed #2. | N/A
| YES | Input Register | 15602 | gModbusUser.Timecode[2] | 1 | Integer | Timecode seed #3. | N/A
| YES | Input Register | 15603 | gModbusUser.Timecode[3] | 1 | Integer | Timecode seed #4. | N/A
| YES | Input Register | 15604 | gModbusUser.Timecode[4] | 1 | Integer | Timecode seed #5. | N/A
| YES | Input Register | 15605 | gModbusUser.Timecode[5] | 1 | Integer | Timecode seed #6. | N/A
| YES | Holding Register | 15600 | gModbusUser.Passcode | 10 | String | Password Entry. 20 characters max. 2 characters per register. | N/A
| YES | Coil | 15501 | gModbusUser.Login | 1 | Bool | Execute security authentication with password. | N/A

## Modbus_Status
MODBUS STATUS WORDS
--Would be frequently/repeatedly accessed.
--Bitpacked for bandwidth efficiency.
INTERNAL TAG NAME | TAG DESCRIPTION | BIT | BIT DEFINITION | NOTES or LOGICAL DERRIVATION
w_NET_Sts_CountdownState | Countdown State | 0.0 | Countdown State | 0=<Not Active>
|  | 0.1 |  | 1=Valve Vent
|  | 0.2 |  | 2=Valve/Pump Vent
|  | 0.3 |  | 3=Low-Pressure Ride-Through
|  | 0.4 |  | 4=Low-Pressure Resume
|  | 0.5 |  | 5=Mold Purge
|  | 0.6 |  | 6=Ramp/Soak Event
|  | 0.7 |  | 7=Cooldown
|  | 0.8 |  | 8=Reboot
|  | 0.9 |  | 9=Auto Restart
|  | 0.10 |  | 10=Mod Valve Homing
|  | 0.11 |  | 11=Mold Purge Bleeddown
0.12
0.13
0.14
0.15
w_NET_Sts_CountdownTimer |  | W
w_NET_Sts_MachineState | Machine State | 0.0 | TCU is Booting Up
|  | 0.1 | TCU is Stopped
|  | 0.2 | TCU is Venting
|  | 0.3 | TCU is Running
|  | 0.4 | TCU is Paused
|  | 0.5 | TCU is Cooling Down
|  | 0.6 | TCU is Mold Purging
|  | 0.7 | TCU is Rebooting
|  | 0.8 | TCU has Warning
|  | 0.9 | TCU in Resetable Alarm
|  | 0.10 | TCU in Non-Resetable Alarm
|  | 0.11 | TCU in High-Temp Non-Resetable Alarm
|  | 0.12 | Spare
|  | 0.13 | Spare
|  | 0.14 | TCU is Operational
|  | 0.15 | TCU Alarm is Silenceable
|  | 0.16 | TCU Alarm is Silenced
|  | 0.17 | Spare
|  | 0.18 | Spare
|  | 0.19 | Spare
|  | 0.20 | Spare
|  | 0.21 | Spare
|  | 0.22 | Spare
|  | 0.23 | Spare
|  | 0.24 | Spare
|  | 0.25 | Spare
|  | 0.26 | Spare
|  | 0.27 | Spare
|  | 0.28 | Spare
|  | 0.29 | Spare
|  | 0.30 | Spare
|  | 0.31 | Spare
w_NET_Sts_WarningAlarm | Highest Prioity Warning/Alarm | 0.0 | Highest Prioity Alarm (USINT)
0.1
0.2
0.3
0.4
0.5
0.6
0.7
|  | 0.8 | Highest Prioity Warning (USINT)
0.9
0.10
0.11
0.12
0.13
0.14
0.15
r_NET_Sts_SetpointTemperature | Setpoint Temp | R | Setpoint Temperature | r_FilteredEffectiveSetpoint
r_NET_Sts_ProcValueTemperature | Effective Process Value Temp | R | Process Value Temperature | r_FilteredEffectiveProcessValue
w_NET_Sts_SetpointState | Setpoint State | 0.0 | Setpoint Source | n_EffectiveSetpointSource
|  | 0.1 |  | 0=Local Main
|  | 0.2 |  | 1=Local Alternative
|  | 0.3 |  | 2=Ramp/Soak
|  | 0.4 |  | 3=Signal
|  | 0.5 |  | 4=Network
0.6
0.7
|  | 0.8 | Main Setpoint Valid
|  | 0.9 | Alternavie Setpoint Valid
|  | 0.10 | Ramp Soak/Setpoint Valid
|  | 0.11 | Signal Setpoint Valid
|  | 0.12 | Network Setpoint Valid
|  | 0.13 | Spare
|  | 0.14 | Spare
|  | 0.15 | Ramp Soak Interim Setpoint Different than Final Setpoint
|  | 0.16 | Active Ramp Soak Step
0.17
0.18
0.19
0.20
0.21
0.22
0.23
|  | 0.24 | Local Sensor Failover Permitted | b_PAR_EnableLocalSensorFailover.CurrentValue
|  | 0.25 | Network Sensor Failover Permitted | b_PAR_EnableNetworkSensorFailover.CurrentValue
|  | 0.26 | Spare
|  | 0.27 | Spare
|  | 0.28 | Spare
|  | 0.29 | Spare
|  | 0.30 | Spare
|  | 0.31 | SetpointFailover Active | b_SubstituteMainSetpoint
w_NET_Sts_ProcessValueState | Process Value State | 0.0 | Effective Process Value Source | n_EffectiveProcessValueSource
|  | 0.1 |  | 0=To Process (Supply)
|  | 0.2 |  | 1=From Process (Return)
|  | 0.3 |  | 2=Average To/From Process
|  | 0.4 |  | 3=Remote
|  | 0.5 |  | 4=Analog Signal
|  | 0.6 |  | 5=Network
0.7
|  | 0.8 | To Process Probe Valid | (NOT b_SupplySensorError) AND (r_IN_SupplyRTD.Implemented)
|  | 0.9 | From Process Probe Valid | (NOT b_ReturnSensorError) AND (r_IN_ReturnRTD.Implemented)
|  | 0.10 | To/From Probe Average Valid | (NOT b_SupplySensorError) AND (NOT b_ReturnSensorError) AND (r_IN_SupplyRTD.Implemented) AND (r_IN_ReturnRTD.Implemented)
|  | 0.11 | Remote Probe Valid | (NOT b_RemoteSensorError) AND (r_IN_RemoteRTD.Implemented)
|  | 0.12 | Analog Signal Valid | (NOT b_AnalogProcessError) AND (r_IN_AnalogProcess.Implemented)
|  | 0.13 | Network Valid | (NOT b_NetworkProcessError) AND (r_NET_ProcessValueTemperature.Implemented)
|  | 0.14 | Spare
|  | 0.15 | Spare
|  | 0.16 | To Process Probe Error | b_SupplySensorError
|  | 0.17 | From Process Probe Error | b_ReturnSensorError
|  | 0.18 | Remote Probe Error | b_RemoteSensorError
|  | 0.19 | Analog Signal Error | b_AnalogProcessError
|  | 0.20 | Network Signal Error | b_NetworkProcessError
|  | 0.21 | Spare
|  | 0.22 | Spare
|  | 0.23 | Spare
|  | 0.24 | Local Sensor Failover Permitted | b_PAR_EnableLocalSensorFailover.CurrentValue
|  | 0.25 | Network Sensor Failover Permitted | b_PAR_EnableNetworkSensorFailover.CurrentValue
|  | 0.26 | Spare
|  | 0.27 | Spare
|  | 0.28 | Spare
|  | 0.29 | Failover: Subbing Supply Sensor | b_SubstituteSupplySensor
|  | 0.30 | Failover: Subbing Return Sensor | b_SubstituteReturnSensor
|  | 0.31 | Failover Active | b_FailoverActiveWarning
w_NET_Sts_TemperatureState | Temperature State | 0.0 | TCU has nearly achieved setpoint
|  | 0.1 | TCU has closely maintained setpoint
|  | 0.2 | TCU is in Steady State
|  | 0.3 | TCU is Neither Heating Nor Cooling
|  | 0.4 | TCU is Heating
|  | 0.5 | TCU is Cooling via Solenoid or Modulating Valve
|  | 0.6 | TCU is Increasing Cooling via Floating Valve
|  | 0.7 | TCU is Decreasing Cooling via Floating Valve
|  | 0.8 | TCU heat/cool is running in external hardwire control.
|  | 0.9 | Spare
|  | 0.10 | Spare
|  | 0.11 | Spare
|  | 0.12 | Spare
|  | 0.13 | Spare
|  | 0.14 | Spare
|  | 0.15 | Spare
|  | 0.16 | Spare
|  | 0.17 | Spare
|  | 0.18 | Spare
|  | 0.19 | Spare
|  | 0.20 | Spare
|  | 0.21 | Spare
|  | 0.22 | Spare
|  | 0.23 | Spare
|  | 0.24 | Heating/Cooling Pct (USINT)
0.25
0.26
0.27
0.28
0.29
0.30
0.31
w_NET_Sts_AlarmMap1 | Alarm Map #1 | 0.0 | Spare | Spare
|  | 0.1 | HMI Connection Failure | b_ALM_IO_HMI_ConnectionFailure
|  | 0.2 | IO Module Link Failure | b_ALM_IO_ModuleLinkFailure
|  | 0.3 | IO Module Hardware Mismatch | b_ALM_IO_HardwareMismatch
|  | 0.4 | IO Module Internal Failure | b_ALM_IO_ModuleInternalFailure
|  | 0.5 | IO Point Failure | b_ALM_IO_PointFailure
|  | 0.6 | Power Supply Voltage Low | b_ALM_PowerSupplyLow
|  | 0.7 | Logic Supply Voltage Low | b_ALM_LogicSupplyLow
|  | 0.8 | Overtemperature | b_ALM_Overtemperature
|  | 0.9 | Heater Contactor Stuck Closed | b_ALM_HeaterContactorStuckClosed
|  | 0.10 | High Temperature - Factory Limit | b_ALM_FactoryTempHigh
|  | 0.11 | Unbranded | b_ALM_Unbranded
|  | 0.12 | Options Not Set | b_ALM_OptionsNotSet
|  | 0.13 | Phase Monitor | b_ALM_PhaseMonitor
|  | 0.14 | Pump Contactor Stuck Closed | b_ALM_PumpContactorStuckClosed
|  | 0.15 | Heater Contactor Stuck Open | b_ALM_HeaterContactorStuckOpen
|  | 0.16 | Pump Contactor Stuck Open | b_ALM_PumpContactorStuckOpen
|  | 0.17 | Pressure Too High | b_ALM_PressureTooHigh
|  | 0.18 | Electrical Panel Too Hot | b_ALM_ElecPanelTooHot
|  | 0.19 | Low Temperature - Factory Limit | b_ALM_FactoryTempLow
|  | 0.20 | Brownout Occurred | b_ALM_Brownout
|  | 0.21 | High Temperature - User Limit | b_ALM_UserTempHigh
|  | 0.22 | Temperature Low - User Limit | b_ALM_UserTempLow
|  | 0.23 | Low Pressure Standby Timeout | b_ALM_LowPressureStandbyTimeout
|  | 0.24 | Low Pressure Strikeout | b_ALM_LowPressureStrikeout
|  | 0.25 | Pump Overload | b_ALM_PumpOverload
|  | 0.26 | Flowmeter Low Flow | b_ALM_FlowmeterLowFlow
|  | 0.27 | Supply RTD - Open Circuit | b_ALM_SupplyRTD_Open
|  | 0.28 | Supply RTD -Short Circuit | b_ALM_SupplyRTD_Shorted
|  | 0.29 | Supply RTD - Channel Error | b_ALM_SupplyRTD_Other
|  | 0.30 | Return RTD - Open Circuit | b_ALM_ReturnRTD_Open
|  | 0.31 | Return RTD - Short Circuit | b_ALM_ReturnRTD_Shorted
w_NET_Sts_AlarmMap2 | Alarm Map #2 | 0.0 | Return RTD - Channel Error | b_ALM_ReturnRTD_Other
|  | 0.1 | Remote RTD - Channel Error | b_ALM_RemoteRTD_Open
|  | 0.2 | Remote RTD - Short Circuit | b_ALM_RemoteRTD_Shorted
|  | 0.3 | Remote RTD - Channel Error | b_ALM_RemoteRTD_Other
|  | 0.4 | Analog Process Input - High Signal | b_ALM_AnaProcInHigh
|  | 0.5 | Analog Process Input - Low Signal | b_ALM_AnaProcInLow
|  | 0.6 | Analog Process Input - Channel Error | b_ALM_AnaProcInOther
|  | 0.7 | Network Process Temperature - High Signal | b_ALM_NetProcHigh
|  | 0.8 | Network Process Temperature - Low Signal | b_ALM_NetProcLow
|  | 0.9 | Network Process Heartbeat Lost | b_ALM_NetProcHeartbeat
|  | 0.10 | Analog Setpoint - High Signal | b_ALM_AnaSP_High
|  | 0.11 | Analog Setpoint - Low Signal | b_ALM_AnaSP_Low
|  | 0.12 | Analog Setpoint - Channel Error | b_ALM_AnaSP_Other
|  | 0.13 | Network Setpoint - High Signal | b_ALM_NetSP_High
|  | 0.14 | Network Setpoint - Low Signal | b_ALM_NetSP_Low
|  | 0.15 | Network Setpoint - Heartbeat Lost | b_ALM_NetSP_Heartbeat
|  | 0.16 | System Pressure Below Minimum | b_ALM_PressureBelowMinimum
|  | 0.17 | System Pressure Not High Enough | b_ALM_PressureNotHighEnough
|  | 0.18 | Return Transducer - High Signal | b_ALM_ReturnTransducerHigh
|  | 0.19 | Return Transducer - Low Signal | b_ALM_ReturnTransducerLow
|  | 0.20 | Return Transducer - Channel Error | b_ALM_ReturnTransducerOther
|  | 0.21 | Supply Transducer - High Signal | b_ALM_SupplyTransducerHigh
|  | 0.22 | Supply Transducer - Low Signal | b_ALM_SupplyTransducerLow
|  | 0.23 | Supply Transducer - Channel Error | b_ALM_SupplyTransducerOther
|  | 0.24 | Analog Flowmeter - High Signal | b_ALM_AnaFlowmeterHigh
|  | 0.25 | Analog Flowmeter - Low Signal | b_ALM_AnaFlowmeterLow
|  | 0.26 | Analog Flowmeter - Channel Error | b_ALM_AnaFlowmeterOther
|  | 0.27 | Process Temperature High Deviation | b_ALM_HighDeviation
|  | 0.28 | Process Temperature Low Deviation | b_ALM_LowDeviation
|  | 0.29 | Network Heartbeat Lost | b_ALM_NetworkHeartbeatLost
|  | 0.30 | Bank Slave Alarm Active | b_ALM_RemoteSlaveAlarmActive
|  | 0.31 | Ramp Soak Paused | b_ALM_RampSoakPaused
w_NET_Sts_AlarmMap3 | Alarm Map #3 | 0.0 | PID Autotune Failed, Starting Control Output Too High | b_ALM_PID_AT_InitOutputTooHigh
|  | 0.1 | PID Autotune Failed, Process Response Too Slow | b_ALM_PID_AT_ProcResponseSlow
|  | 0.2 | PID Autotune Failed, Time Constant Not Found | b_ALM_PID_AT_TimeConstNotFound
|  | 0.3 | PID Autotune Failed, Process Limit Exceeded | b_ALM_PID_AT_TimeConstNotFound
|  | 0.4 | Spare | Spare
|  | 0.5 | Spare | Spare
|  | 0.6 | Spare | Spare
|  | 0.7 | Spare | Spare
|  | 0.8 | Spare | Spare
|  | 0.9 | Spare | Spare
|  | 0.10 | Spare | Spare
|  | 0.11 | Spare | Spare
|  | 0.12 | Spare | Spare
|  | 0.13 | Spare | Spare
|  | 0.14 | Spare | Spare
|  | 0.15 | Spare | Spare
|  | 0.16 | Spare | Spare
|  | 0.17 | Spare | Spare
|  | 0.18 | Spare | Spare
|  | 0.19 | Spare | Spare
|  | 0.20 | Spare | Spare
|  | 0.21 | Spare | Spare
|  | 0.22 | Spare | Spare
|  | 0.23 | Spare | Spare
|  | 0.24 | Spare | Spare
|  | 0.25 | Spare | Spare
|  | 0.26 | Spare | Spare
|  | 0.27 | Spare | Spare
|  | 0.28 | Spare | Spare
|  | 0.29 | Spare | Spare
|  | 0.30 | Spare | Spare
|  | 0.31 | Spare | Spare
w_NET_Sts_AlarmMap4 | Alarm Map #4 | 0.0 | Spare | Spare
|  | 0.1 | Spare | Spare
|  | 0.2 | Spare | Spare
|  | 0.3 | Spare | Spare
|  | 0.4 | Spare | Spare
|  | 0.5 | Spare | Spare
|  | 0.6 | Spare | Spare
|  | 0.7 | Spare | Spare
|  | 0.8 | Spare | Spare
|  | 0.9 | Spare | Spare
|  | 0.10 | Spare | Spare
|  | 0.11 | Spare | Spare
|  | 0.12 | Spare | Spare
|  | 0.13 | Spare | Spare
|  | 0.14 | Spare | Spare
|  | 0.15 | Spare | Spare
|  | 0.16 | Spare | Spare
|  | 0.17 | Spare | Spare
|  | 0.18 | Spare | Spare
|  | 0.19 | Spare | Spare
|  | 0.20 | Spare | Spare
|  | 0.21 | Spare | Spare
|  | 0.22 | Spare | Spare
|  | 0.23 | Spare | Spare
|  | 0.24 | Spare | Spare
|  | 0.25 | Spare | Spare
|  | 0.26 | Spare | Spare
|  | 0.27 | Spare | Spare
|  | 0.28 | Spare | Spare
|  | 0.29 | Spare | Spare
|  | 0.30 | Spare | Spare
|  | 0.31 | Spare | Spare
w_NET_Sts_WarningMap1 | Warning Map #1 | 0.0 | Spare | Spare
|  | 0.1 | Pump Overload | b_WRN_PumpOverload
|  | 0.2 | Flowmeter - Low Flow | b_WRN_FlowmeterLowFlow
|  | 0.3 | Failover Active: Supply RTD --> Return RTD, due to Supply RTD - Open circuit | b_WRN_FO_SupToRet_SupRTD_Open
|  | 0.4 | Failover Active: Supply RTD --> Return RTD, due to Supply RTD - Short circuit | b_WRN_FO_SupToRet_SupRTD_Shorted
|  | 0.5 | Failover Active: Supply RTD --> Return RTD, due to Supply RTD - Channel error | b_WRN_FO_SupToRet_SupRTD_Other
|  | 0.6 | Failover Active: Return RTD --> Supply RTD, due to Return RTD - Open circuit | b_WRN_FO_RetToSup_RetRTD_Open
|  | 0.7 | Failover Active: Return RTD --> Supply RTD, due to Return RTD - Short circuit | b_WRN_FO_RetToSup_RetRTD_Shorted
|  | 0.8 | Failover Active: Return RTD --> SupplyRTD, due to Return RTD - Channel error | b_WRN_FO_RetToSup_RetRTD_Other
|  | 0.9 | Failover Active: Remote RTD --> Return RTD, due to Remote RTD - Open circuit | b_WRN_FO_RemToRet_RemRTD_Open
|  | 0.10 | Failover Active: Remote RTD --> Return RTD, due to Remote RTD - Short circuit | b_WRN_FO_RemToRet_RemRTD_Shorted
|  | 0.11 | Failover Active: Remote RTD --> Return RTD, due to Remote RTD - Channel error | b_WRN_FO_RemToRet_RemRTD_Other
|  | 0.12 | Failover Active: Analog Process Input --> Return RTD, due to Analog Process Input - Signal high | b_WRN_FO_AnaToRet_AnaProcInHigh
|  | 0.13 | Failover Active: Analog Process Input --> Return RTD, due to Analog Process Input - Signal low | b_WRN_FO_AnaToRet_AnaProcInLow
|  | 0.14 | Failover Active: Analog Process Input --> Return RTD, due to Analog Process Input - Channel error | b_WRN_FO_AnaToRet_AnaProcInOther
|  | 0.15 | Failover Active: Network Process Temperature --> Return RTD, due to Network Process Temperature - Signal high | b_WRN_FO_NetToRet_NetProcHigh
|  | 0.16 | Failover Active: Network Process Temperature --> Return RTD, due to Network Process Temperature - Signal low | b_WRN_FO_NetToRet_NetProcLow
|  | 0.17 | Failover Active: Network Process Temperature --> Return RTD, due to Network Process Temperature - Heartbeat lost | b_WRN_FO_NetToRet_NetProcHB
|  | 0.18 | Failover Active: Analog Setpoint Input --> Main Setpoint, due to Analog Setpoint - Signal high | b_WRN_FO_AnaToMain_AnaSP_High
|  | 0.19 | Failover Active: Analog Setpoint Input --> Main Setpoint, due to Analog Setpoint - Signal low | b_WRN_FO_AnaToMain_AnaSP_Low
|  | 0.20 | Failover Active: Analog Setpoint Input --> Main Setpoint, due to Analog Setpoint - Channel error | b_WRN_FO_AnaToMain_AnaSP_Other
|  | 0.21 | Failover Active: Network Setpoint --> Main Setpoint, due to Network Setpoint - Signal high | b_WRN_FO_NetToMain_NetSP_High
|  | 0.22 | Failover Active: Network Setpoint --> Main Setpoint, due to Network Setpoint - Signal low | b_WRN_FO_NetToMain_NetSP_Low
|  | 0.23 | Failover Active: Network Setpoint --> Main Setpoint, due to Network Setpoint - Heartbeat lost | b_WRN_FO_NetToMain_NetSP_HB
|  | 0.24 | System Pressure Below Minimum | b_WRN_PressureBelowMinimum
|  | 0.25 | System Pressure Not High Enough | b_WRN_PressureNotHighEnough
|  | 0.26 | Setpoint Too High For Pressure | b_WRN_SetpointTooHighForPressure
|  | 0.27 | Supply Transducer - Signal High | b_WRN_SupplyTransducerHigh
|  | 0.28 | Supply Transducer - Signal Low | b_WRN_SupplyTransducerLow
|  | 0.29 | Supply Transducer - Channel Error | b_WRN_SupplyTransducerOther
|  | 0.30 | Supply RTD - Open circuit | b_WRN_SupplyRTD_Open
|  | 0.31 | Supply RTD - Short circuit | b_WRN_SupplyRTD_Shorted
w_NET_Sts_WarningMap2 | Warning Map #2 | 0.0 | Supply RTD - Channel error | b_WRN_SupplyRTD_Other
|  | 0.1 | Return RTD - Open circuit | b_WRN_ReturnRTD_Open
|  | 0.2 | Return RTD - Short circuit | b_WRN_ReturnRTD_Shorted
|  | 0.3 | Return RTD - Channel error | b_WRN_ReturnRTD_Other
|  | 0.4 | Analog Flowmeter - Signal High | b_WRN_AnaFlowmeterHigh
|  | 0.5 | Analog Flowmeter- Signal Low | b_WRN_AnaFlowmeterLow
|  | 0.6 | Analog Flowmeter - Channel Error | b_WRN_AnaFlowmeterOther
|  | 0.7 | Too Many Flash Memory Writes | b_WRN_FlashMemoryWrites
|  | 0.8 | High Temperature Deviation | b_WRN_HighDeviation
|  | 0.9 | Low Temperature Deviation | b_WRN_LowDeviation
|  | 0.10 | Network Heartbeat Lost | b_WRN_NetworkHeartbeatLost
|  | 0.11 | Remote Slave Warning Active | b_WRN_RemoteSlaveWarningActive
|  | 0.12 | Too Frequent Heater Cycles | b_WRN_TooManyHeaterCycles
|  | 0.13 | Worn Out Heater Contactor | b_WRN_WornOutHeaterContactor
|  | 0.14 | Clock Not Set | b_WRN_ClockNotSet
|  | 0.15 | Spare | Spare
|  | 0.16 | Spare | Spare
|  | 0.17 | Spare | Spare
|  | 0.18 | Spare | Spare
|  | 0.19 | Spare | Spare
|  | 0.20 | Spare | Spare
|  | 0.21 | Spare | Spare
|  | 0.22 | Spare | Spare
|  | 0.23 | Spare | Spare
|  | 0.24 | Spare | Spare
|  | 0.25 | Spare | Spare
|  | 0.26 | Spare | Spare
|  | 0.27 | Spare | Spare
|  | 0.28 | Spare | Spare
|  | 0.29 | Spare | Spare
|  | 0.30 | Spare | Spare
|  | 0.31 | Spare | Spare
w_NET_Sts_WarningMap3 | Warning Map #3 | 0.0 | Spare | Spare
|  | 0.1 | Spare | Spare
|  | 0.2 | Spare | Spare
|  | 0.3 | Spare | Spare
|  | 0.4 | Spare | Spare
|  | 0.5 | Spare | Spare
|  | 0.6 | Spare | Spare
|  | 0.7 | Spare | Spare
|  | 0.8 | Spare | Spare
|  | 0.9 | Spare | Spare
|  | 0.10 | Spare | Spare
|  | 0.11 | Spare | Spare
|  | 0.12 | Spare | Spare
|  | 0.13 | Spare | Spare
|  | 0.14 | Spare | Spare
|  | 0.15 | Spare | Spare
|  | 0.16 | Spare | Spare
|  | 0.17 | Spare | Spare
|  | 0.18 | Spare | Spare
|  | 0.19 | Spare | Spare
|  | 0.20 | Spare | Spare
|  | 0.21 | Spare | Spare
|  | 0.22 | Spare | Spare
|  | 0.23 | Spare | Spare
|  | 0.24 | Spare | Spare
|  | 0.25 | Spare | Spare
|  | 0.26 | Spare | Spare
|  | 0.27 | Spare | Spare
|  | 0.28 | Spare | Spare
|  | 0.29 | Spare | Spare
|  | 0.30 | Spare | Spare
|  | 0.31 | Spare | Spare
w_NET_Sts_WarningMap4 | Warning Map #4 | 0.0 | Spare | Spare
|  | 0.1 | Spare | Spare
|  | 0.2 | Spare | Spare
|  | 0.3 | Spare | Spare
|  | 0.4 | Spare | Spare
|  | 0.5 | Spare | Spare
|  | 0.6 | Spare | Spare
|  | 0.7 | Spare | Spare
|  | 0.8 | Spare | Spare
|  | 0.9 | Spare | Spare
|  | 0.10 | Spare | Spare
|  | 0.11 | Spare | Spare
|  | 0.12 | Spare | Spare
|  | 0.13 | Spare | Spare
|  | 0.14 | Spare | Spare
|  | 0.15 | Spare | Spare
|  | 0.16 | Spare | Spare
|  | 0.17 | Spare | Spare
|  | 0.18 | Spare | Spare
|  | 0.19 | Spare | Spare
|  | 0.20 | Spare | Spare
|  | 0.21 | Spare | Spare
|  | 0.22 | Spare | Spare
|  | 0.23 | Spare | Spare
|  | 0.24 | Spare | Spare
|  | 0.25 | Spare | Spare
|  | 0.26 | Spare | Spare
|  | 0.27 | Spare | Spare
|  | 0.28 | Spare | Spare
|  | 0.29 | Spare | Spare
|  | 0.30 | Spare | Spare
|  | 0.31 | Spare | Spare
r_NET_SetpointTemperature.CurrentValue | Network Setpoint | R | Readback of network setpoint value (r_NET_Cmd_SetpointTemperature).
r_NET_ProcessValueTemperature.CurrentValue | Network Temp | R | Readback of network process value. Comprised of r_NET_Cmd_ProcValueTemp added to its calibration value r_PAR_NetworkProcessCalOffset.CurrentValue.
w_NET_MSM_TSM_State | MSM State Number | 0.0 | n_HMI_MSM_State | 0=Unknown
|  | 0.1 |  | 1=Booting
|  | 0.2 |  | 2=Starting
|  | 0.3 |  | 3=Preparing to Stop
|  | 0.4 |  | 4=Stopped
|  | 0.5 |  | 5=Preparing to Vent
|  | 0.6 |  | 6=Valve Vent
|  | 0.7 |  | 7=Valve/Pump Vent
8=Preparing to Run
9=Running
10=Low Pressure Pause
11=Cooldown to Stop
12=Mold Purging On
13=Spare
14=Spare
15=Spare
16=Preparing to Alarm
17=Alarm (Resettable)
18=Alarm(Non-Resettable)
19=Alarm(Overtemp)
20=Alarm Resetting
21=Reboot
| TSM State Number | 0.8 | n_HMI_TSM_State | 0=Unknown
|  | 0.9 |  | 1=Booting
|  | 0.10 |  | 2=Init
|  | 0.11 |  | 3=Stop
|  | 0.12 |  | 4=Vent
|  | 0.13 |  | 5=Solenoid Valve, No Action
|  | 0.14 |  | 6=Solenoid Valve, Heating
|  | 0.15 |  | 7=Solenoid Valve, Cooling
8=Floating Valve, No Action
9=Floating Valve, Heating
10=Floating Valve, Less Cool
11=Floating Valve, Less Cool, Prepare to Open
12=Floating Valve, More Cool
13=Floating Valve, More Cool, Prepare to Close
14=Modulating Valve, No Action
15=Modulating Valve, Heating
16=Modulating Valve, Cooling
17=Emergency Cooling (all valve types)
n_HD_RebootMessage | Reboot Message | DW |  | 0=Preparing To Reboot
1=Loading User Defaults
2=Loading Factory Defaults
3=Changing Units
4=Changing Branding
5=Changing Flowmeter
6=Changing Network
st_CurrentLocalDateTime.MsSincePowerup | Milliseconds since last powerup | DW
st_CurrentLocalDateTime.Month | Month | W
st_CurrentLocalDateTime.Day | Date | W
st_CurrentLocalDateTime.Year | Year | W |  | 4-digit
st_CurrentLocalDateTime.Hour | Hour | W |  | 24-hour format
st_CurrentLocalDateTime.Minute | Minute | W
st_CurrentLocalDateTime.Second | Second | W
st_CurrentLocalDateTime.DayOfWeek | Day of the Week | W |  | 0=<unknown>
1=Monday
2=Tuesday
3=Wednesday
4=Thursday
5=Friday
6=Saturday
7=Sunday
st_CurrentLocalDateTime.TimezoneOffset |  | DW |  | Real
st_CurrentLocalDateTime.MsSincePowerup |  | DW
st_CurrentLocalDateTime.MsSinceBootup |  | DW
st_CurrentLocalDateTime.DstActive |  | W |  | Not currently implemented.
st_CurrentLocalDateTime.DstAutoChangeActive |  | Bit |  | Not currently implemented.
w_NET_IN_Value1 | Physical digital input values. | 0.0 | b_IN_PhaseMonitor | 0=Input OFF 1=input ON
|  | 0.1 | b_IN_PumpOverload
|  | 0.2 | b_IN_PumpContactorAux
|  | 0.3 | b_IN_HeaterContactorAux
|  | 0.4 | b_IN_PressureSwitch
|  | 0.5 | b_IN_HeaterHighTemp
|  | 0.6 | b_IN_Flowswitch
|  | 0.7 | b_IN_RemoteStart
|  | 0.8 | b_IN_SetpointSelectAdvance
|  | 0.9 | Spare
|  | 0.10 | Spare
|  | 0.11 | Spare
|  | 0.12 | Spare
|  | 0.13 | Spare
|  | 0.14 | Spare
|  | 0.15 | Spare
w_NET_OUT_Value1 | Physical digital output values. | 0.0 | b_OUT_AlarmSilenceable | 0=Input OFF 1=input ON
|  | 0.1 | b_OUT_PumpContactor
|  | 0.2 | b_OUT_HeaterContactor
|  | 0.3 | b_OUT_HeaterSSR
|  | 0.4 | b_OUT_AlarmNonSilenceable
|  | 0.5 | b_OUT_MoldPurge
|  | 0.6 | b_OUT_CoolingValveOpen
|  | 0.7 | b_OUT_Vent
|  | 0.8 | b_OUT_FillValve
|  | 0.9 | Spare
|  | 0.10 | Spare
|  | 0.11 | Spare
|  | 0.12 | Spare
|  | 0.13 | Spare
|  | 0.14 | Spare
|  | 0.15 | Spare
w_NET_IN_Error1 | Physical digital input errors. | 0.0 | b_IN_PhaseMonitor | 0=OK 1=Error
|  | 0.1 | b_IN_PumpOverload
|  | 0.2 | b_IN_PumpContactorAux
|  | 0.3 | b_IN_HeaterContactorAux
|  | 0.4 | b_IN_PressureSwitch
|  | 0.5 | b_IN_HeaterHighTemp
|  | 0.6 | b_IN_Flowswitch
|  | 0.7 | b_IN_RemoteStart
|  | 0.8 | b_IN_SetpointSelectAdvance
|  | 0.9 | Spare
|  | 0.10 | Spare
|  | 0.11 | Spare
|  | 0.12 | Spare
|  | 0.13 | Spare
|  | 0.14 | Spare
|  | 0.15 | Spare
w_NET_OUT_Error1 | Physical digital output errors. | 0.0 | b_OUT_AlarmSilenceable | 0=OK 1=Error
|  | 0.1 | b_OUT_PumpContactor
|  | 0.2 | b_OUT_HeaterContactor
|  | 0.3 | b_OUT_HeaterSSR
|  | 0.4 | b_OUT_AlarmNonSilenceable
|  | 0.5 | b_OUT_MoldPurge
|  | 0.6 | b_OUT_CoolingValveOpen
|  | 0.7 | b_OUT_Vent
|  | 0.8 | b_OUT_FillValve
|  | 0.9 | Spare
|  | 0.10 | Spare
|  | 0.11 | Spare
|  | 0.12 | Spare
|  | 0.13 | Spare
|  | 0.14 | Spare
|  | 0.15 | Spare
w_NET_Signal_Error1 | Supply RTD Status | .0-.3 | n_HD_SupplyTempError | 0=Ok
| Return RTD Status | .4-.7 | n_HD_ReturnTempError | 1=Open (applicable for RTD signals only)
| Remote RTD Status | .8-.11 | n_HD_RemoteTempError | 2=Short (applicable for RTD signals only)
| Analog Process Status | .12-.15 | n_HD_AnalogProcessTempError | 3=Error
| Network Process Status | .16-.19 | n_HD_NetworkProcessTempError | 4=Not Used
| Analog Setpoint Status | .20-.23 | n_HD_AnalogSetpointError | 5=High Circuit (applicable for analog and network signals only)
| Network Setpoint Status | .24-.27 | n_HD_NetworkSetpointError | 6=Low Circuit (applicable for analog and network signals only)
| Supply Pressure Transducer Status | .28-.31 | n_HD_SupplyTransducerError | 7=Heartbeat Error (applicable for network signals only)
w_NET_Signal_Error2 | Return Pressure Transducer Status | .0-.3 | n_HD_ReturnTransducerError
| Flowmeter (analog or pulse) Status | .4-.7 | n_HD_FlowrateError
|  | .8-.11 | Spare
|  | .12-.15 | Spare
|  | .16-.19 | Spare
|  | .20-.23 | Spare
|  | .24-.27 | Spare
|  | .28-.31 | Spare

## Modbus_Command
MODBUS COMMAND WORDS
--Could be frequently/repeatedly accessed.
--Bitpacked for bandwidth efficiency.
INTERNAL TAG NAME | TAG DESCRIPTION | BIT | BIT DEFINITION | NOTES or LOGICAL DERRIVATION | Implemented as OPC-UA Method?
w_NET_Cmd_MachineState | Machine State | 0.0 | Toggle TCU Start/Stop |  | NO
|  | 0.1 | Initiate TCU Stop |  | YES
|  | 0.2 | Initiate TCU Start |  | YES
|  | 0.3 | Initiate Mold Purge | Only when stopped. | YES
|  | 0.4 | Initiate AutoCoolStop | Only when stopped. | YES
|  | 0.5 | Initiate Fault Reset |  | YES
|  | 0.6 | Initiate Auto Tune (future) | Not yet implemented. | YES (future)
|  | 0.7 | Accept Auto Tune Results (future) | Not yet implemented. | YES (future)
|  | 0.8 | Initiate Hot Reboot (State Machine Only) | Only when stopped. | YES
|  | 0.9 | Load User Defaults | Only when stopped. | YES
|  | 0.10 | Load Factory Defaults | Only when stopped. | YES
|  | 0.11 | Initiate Alarm Silence | Only when an alarm is present. | YES
|  | 0.12 | Reset All Health Counters | Only when stopped. | YES
|  | 0.13 | Reset Pump Health | Only when stopped. | YES
|  | 0.14 | Reset Pump Contactor Health | Only when stopped. | YES
|  | 0.15 | Reset Heater Health | Only when stopped. | YES
|  | 0.16 | Reset Heater Contactor Health | Only when stopped. | YES
|  | 0.17 | Reset Heater SSR Health | Only when stopped. | YES
|  | 0.18 | Reset Cooling Valve Health | Only when stopped. | YES
|  | 0.19 | Reset Max Loop Time | Anytime | YES
|  | 0.20 | Initiate Warm Reboot (Hardwre Reboot) | Only when stopped. | YES
|  | 0.21 | Spare |  | N/A
|  | 0.22 | Spare |  | N/A
|  | 0.23 | Spare |  | N/A
|  | 0.24 | Spare |  | N/A
|  | 0.25 | Spare |  | N/A
|  | 0.26 | Spare |  | N/A
|  | 0.27 | Spare |  | N/A
|  | 0.28 | Spare |  | N/A
|  | 0.29 | Inhibit venting sequence regardless of temperature. | Must be set before or when run is initiated, can be set while venting is active to abort venting and go right into run. | YES
|  | 0.30 | Require venting sequence regardless of temperature. | Must be set before or when run is initiated. | YES
|  | 0.31 | Ramp/Soak: Go To Next Step (if "Trigger For Next Step" set to "Network Trigger") |  | YES
w_NET_NetworkState | Network State | 0.0 | Heartbeat | Default State = 0. | OPC-UA method can be used to represent a heartbeat/response.
|  | 0.1 |  | Remote writes 2.
|  | 0.2 |  | Local writes 1.
0.3
0.4
0.5
0.6
0.7
|  | 0.8 | Spare
|  | 0.9 | Spare
|  | 0.10 | Spare
|  | 0.11 | Spare
|  | 0.12 | Spare
|  | 0.13 | Spare
|  | 0.14 | Spare
|  | 0.15 | Spare
r_NET_Cmd_SetpointTemperature | Network Setpoint Temp | R | Network Generated Setpoint | Not yet implemented. | N/A - Analog Value
r_NET_Cmd_ProcessValueTemperature | Process Value Temp (Network) | R | Network Measured Process Value | Not yet implemented. | N/A - Analog Value
w_NET_Cmd_SetpointState | Setpoint State | 0.0 | Use external PID | b_NET_UseExternalPID. Not yet implemented. | NO
|  | 0.1 | Remote More Cool Direct Control | b_NET_MoreCoolDirectControl. Not yet implemented. | NO
|  | 0.2 | Remote Less Cool Direct Control | b_NET_LessCoolDirectControl. Not yet implemented. | NO
|  | 0.3 | Remote Heat Direct Control | b_NET_HeatDirectControl. Not yet implemented. | NO
|  | 0.4 | Spare |  | N/A
|  | 0.5 | Spare |  | N/A
|  | 0.6 | Spare |  | N/A
|  | 0.7 | Spare |  | N/A
|  | 0.8 | Remote More Cool Pct | b_NET_RemoteMoreCoolLevel, use in conjuntion with percent in last byte. Not yet implemented. | NO
|  | 0.9 | Remote Less Cool Pct | b_NET_RemoteLessCoolLevel, use in conjuntion with percent in last byte. Not yet implemented. | NO
|  | 0.10 | Remote Heat Pct | b_NET_RemoteHeatLevel, use in conjuntion with percent in last byte. Not yet implemented. | NO
|  | 0.11 | Spare |  | N/A
|  | 0.12 | Spare |  | N/A
|  | 0.13 | Spare |  | N/A
|  | 0.14 | Spare |  | N/A
|  | 0.15 | Spare |  | N/A
|  | 0.16 | Initiate Pressure Relief | b_NET_RelievePressure | YES
|  | 0.17 | Initiate Main Setpoint as Setpoint Source |  | YES
|  | 0.18 | Initiate Alternative Setpoint as Setpoint Source |  | YES
|  | 0.19 | Initiate Ramp/Soak as Setpoint Source |  | YES
|  | 0.20 | Spare |  | N/A
|  | 0.21 | Spare |  | N/A
|  | 0.22 | Spare |  | N/A
|  | 0.23 | Spare |  | N/A
|  | 0.24 | Heating/Cooling Pct | n_NET_RemoteHeatCoolLevel. Not yet implemented. | N/A - Analog Value
0.25
0.26
0.27
0.28
0.29
0.30
0.31
w_NET_Cmd_ProcessValueState | Process Value State | 0.0 | Spare | Not yet implemented. | N/A
|  | 0.1 | Spare |  | N/A
|  | 0.2 | Spare |  | N/A
|  | 0.3 | Spare |  | N/A
|  | 0.4 | Spare |  | N/A
|  | 0.5 | Spare |  | N/A
|  | 0.6 | Spare |  | N/A
|  | 0.7 | Spare |  | N/A
|  | 0.8 | Spare |  | N/A
|  | 0.9 | Spare |  | N/A
|  | 0.10 | Spare |  | N/A
|  | 0.11 | Spare |  | N/A
|  | 0.12 | Spare |  | N/A
|  | 0.13 | Spare |  | N/A
|  | 0.14 | Spare |  | N/A
|  | 0.15 | Spare |  | N/A
w_NET_Cmd_UserInteraction | User Interaction | 0.0 | Initiate Beep |  | YES
|  | 0.1 | Screen Backlight Flash |  | YES
|  | 0.2 | Screen Backlight On |  | YES
|  | 0.3 | Screen Backlight Off |  | YES
|  | 0.4 | Chirp Silenceable Alarm Output (only works in IS, SP, IV, V1, V2, IR, RN, LP, CD, MP states) |  | YES
|  | 0.5 | Spare |  | N/A
|  | 0.6 | Spare |  | N/A
|  | 0.7 | Spare |  | N/A
|  | 0.8 | Spare |  | N/A
|  | 0.9 | Spare |  | N/A
|  | 0.10 | Spare |  | N/A
|  | 0.11 | Spare |  | N/A
|  | 0.12 | Spare |  | N/A
|  | 0.13 | Spare |  | N/A
|  | 0.14 | Spare |  | N/A
|  | 0.15 | Spare |  | N/A
w_NET_BankedUnitAssignment | Banking Setup | 0.0 | Total Number of Machines in bank. |  | NO
0.1
0.2
0.3
0.4
0.5
0.6
0.7
|  | 0.8 | Order Assignment of this Machine in bank. |  | NO
0.9
0.10
0.11
0.12
0.13
0.14
0.15

## OPCUA
OPC-UA DEFINITION
| ENABLED | CATEGORY | INTERNAL TAG NAME | UNITS INDEX | DISPLAY NAME | DESCRIPTION | INTERNAL UNITS | NOTES
Command Words
| FALSE | COMMANDS | r_NET_Cmd_ProcValueTemp | 2 | r_NET_Cmd_ProcessValueTemp | Not currently enabled. | °C | Not currently enabled.
| FALSE | COMMANDS | r_NET_Cmd_SetpointTemperature | 2 | r_NET_Cmd_SetpointTemperature | Not currently enabled. | °C | Not currently enabled.
| TRUE | COMMANDS | w_NET_Cmd_MachineState |  | w_NET_Cmd_MachineState | Bit-packed command word. Bit 0=Toggle TCU Start/Stop; Bit 1=Initiate TCU Stop; Bit 2=Initiate TCU Start; Bit 3=Initiate Mold Purge; Bit 4=Initiate Auto Cool Stop; Bit 5=Initiate Fault Reset; Bit 6=Initiate Auto Tune (not yet implemented); Bit 7=Accept Auto Tune Results (not yet implemented); Bit 8=Initiate Hot Reboot; Bit 9=Load User Defaults; Bit 10=Load Factory Defaults (depricated); Bit 11=Initiate Alarm Silence; Bit 12=Reset All Health Counters; Bit 13=Reset Pump Health; Bit 14=Reset Pump Contactor Health; Bit 15=Reset Heater Health; Bit 16=Reset Heater Contactor Health; Bit 17=Reset Heater SSR Health; Bit 18=Reset Cooling Valve Health; Bit 19=Reset Max Loop Time; Bit 20=Initiate Warm Reboot; Bit 31=Ramp/Soak: Go to next Step (if "Trigger For Next Step" is set to "Network Trigger"). | N/A | See Modbus_Command sheet for details.
| FALSE | COMMANDS | w_NET_Cmd_ProcessValueState |  | w_NET_Cmd_ProcessValueState | See Modbus_Command sheet for details, but not currently enabled. | N/A | See Modbus_Command sheet for details, but not currently enabled.
| TRUE | COMMANDS | w_NET_Cmd_SetpointState |  | w_NET_Cmd_SetpointState | Bit/Byte-packed command word. Bit 0=Use external PID (not yet implemented); Bit 1=Remote More Cool Direct Control (not yet implemented); Bit 2=Remote Less Cool Direct Control (not yet implemented); Bit 3=Remote Heat Direct Control (not yet implemented); Bit 8=Remote More Cool Pct (not yet implemented); Bit 9=Remote Less Cool Pct (not yet implemented); Bit 10=Remote Heat Pct (not yet implemented); Bit 16=Initiate Pressure Relief;; Bit 17=Initiate Main Setpoint as Setpoint Source; 18=Initiate Alternative Setpoint as Setpoint Source; 19=Initiate Ramp/Soak as Setpoint Source; Bits 24-31=8-bit Heating/Cooling Pct (Signed Integer). | N/A | See Modbus_Command sheet for details.
| TRUE | COMMANDS | w_NET_Cmd_UserInteraction |  | w_NET_Cmd_UserInteraction | Bit-packed command word. Bit 0=Initiate Beep; Bit 1=Screen Backlight Flash; Bit 2=Screen Backlight On; Bit 3=Screen Backlight Off | N/A | See Modbus_Command sheet for details.
| TRUE | COMMANDS | w_NET_NetworkState |  | w_NET_NetworkState | Byte-packed enumerated command word. Bits 0-6=Heartbeat (default state=0, remote writes "2", local writes "1"). | N/A | See Modbus_Command sheet for details.
Status Words
| TRUE | STATUS | w_NET_MSM_TSM_State |  | w_NET_MasterStateMachine_TemperatureStateMachine_State | Byte-packed enumerated status word. Bits 0-7=Machine State (0=Unknown, 1=Booting, 2=Starting, 3=Preparing to Stop, 4=Stopped, 5=Preparing to Vent, 6=Valve Vent, 7=Valve/Pump Vent, 8=Preparing to Run, 9=Running, 10=Low Pressure Pause, 11=Countdown to Stop, 12=Mold Purge Active, 13=Spare, 14=Spare, 15=Spare, 16=Preparing to Alarm, 17=Alarm (resettable), 18=Alarm (non-resettable), 19=Alarm (overtemperature), 20=Alarm Resetting, 21=Reboot); Bits 8-15=Temperature State (0=Unknon, 1=Booting, 2=Init, 3=Stop, 4=Vent, 5=Solenoid Valve, No Action, 6=Solenoid Valve, Heating, 7=Solenoid Valve, Cooling, 8=Floating Valve, No Action, 9=Floating Valve, Heating, 10=Floating Valve, Less Cool, 11=Floating Valve, Less Cool, Prepare to Open, 12=Floating Valve, More Cool, 13=Floating Valve, More Cool, Prepare to Close, 14=Modulating Valve, No Action, 15=Modulating Valve, Heating, 16=Modulating Valve, Cooling, 17=Emergency Cooling (all valve types). | <enumeration> | See Modbus_Status sheet for details (byte enumeration).
| TRUE | STATUS | r_NET_ProcessValueTemperature.CurrentValue | 2 | r_NET_ProcessValueTemperature.CurrentValue | Readback of network-provided process value temperature. | °C | See Modbus_Status sheet for details.
| TRUE | STATUS | r_NET_SetpointTemperature.CurrentValue | 2 | r_NET_SetpointTemperature.CurrentValue | Readback of network-provided setpoint temperature. | °C | See Modbus_Status sheet for details.
| TRUE | STATUS | r_NET_Sts_ProcValueTemperature | 2 | r_NET_Status_ProcessValueTemperature | The effective, filtered process value temperature. | °C | See Modbus_Status sheet for details.
| TRUE | STATUS | r_NET_Sts_SetpointTemperature | 2 | r_NET_Status_SetpointTemperature | The effective, filtered setpoint temperature. | °C | See Modbus_Status sheet for details.
| TRUE | STATUS | w_NET_Sts_CountdownState |  | w_NET_Status_CountdownState | Byte-packed enumerated status word. Bits 0-7=Countdown State (0=Not Active, 1=Valve Vent, 2=Valve/Pump Vent, 3=Low-Pressure Ride-Through, 4=Low-Pressure Resume, 5=Mold Purge, 6=Ramp/Soak Event, 7=Cooldown, 8=Reboot, 9=Auto Restart, 10=Mod Valve Homing). | <enumeration> | See Modbus_Status sheet for details (byte enumeration).
| TRUE | STATUS | w_NET_Sts_CountdownTimer | 8 | w_NET_Status_CountdownTimer | How many seconds are left before an event occurs. | seconds | See Modbus_Status sheet for details (word).
| TRUE | STATUS | w_NET_Sts_MachineState |  | w_NET_Status_MachineState | Bit-packed status double-word: Bit 0=TCU Booting Up, Bit 1=TCU is Stopped, Bit 2=TCU is Venting, Bit 3=TCU is Running, Bit 4=TCU is Paused, Bit 5=TCU is Cooling Down, Bt 6=TCU is Mold Purging, Bit 7=TCU is Rebooting, Bit 8=TCU has Warning, Bit 9=TCU is Resettable Alarm, Bit 10=TCU is Non-Resetable Alarm, Bit 11=TCU in High-Temp Non-Resettable Alarm, 12=Spare, 13=Spare, 14=TCU is Operational, 15=TCU Alarm is Silenceable, 16=TCU Alarm is Silenced. | <enumeration> | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_Sts_ProcessValueState |  | w_NET_Status_ProcessValueState | Bit/Byte-packed enumerated status double-word: Bits 0-7=Effective Process Value Source (0=To Process (Supply), 1=From Process (Return), 2=Average of To/From Process, 3=Remote, 4=Analog Signal, 5=Network; Bit 8=To Process Probe Valid, Bit 9=From Process Probe Valid, Bit 10=To/From Prove Average Valid, 11=Remote Probe Valid, 12=Analog Signal Valid, 13=Network Valid, 14=Spare, 15=Spare, 16=To Process (Supply) Probe Error, 17=From Process (Return) Probe Error, 18=Remote Probe Error, 19=Analog Signal Error, 20-Network Signal Error, 21=Spare, 22=Spare, 23=Spare, 24=Local Sensor Failover Permitted, 25=Network Sensor Failover Permitted, 26=Spare, 27=Spare, 28=Spare, 29=Failover: Subbing To Process (Supply) Sensor, 30=Failover: Subbing From Process (Return) Sensor, 31=Failover Active. | <enumeration> | See Modbus_Status sheet for details (byte enumeration and bit-packed).
| TRUE | STATUS | w_NET_Sts_SetpointState |  | w_NET_Status_SetpointState | Bit/Byte-packed enumerated status double-word: Bits 0-7=Setpoint Source (0=Local Main, 1=Local Alternative, 2=Ramp/Soak, 3=Signal, 4=Network); Bit 8=Main Setpoint Valid; Bit 9=Alternative Setpoint Valid; Bit 10=Ramp/Soak Setpoint Valid; Bit 11=Signal Setpoint Valid; Bit 12=Network Setpoint Valid; Bit 13=Spare; Bit 14=Spare; Bit 15=Ramp/Soak Interim Setpoint Different than Final Setpoint; Bits 16-23=Active Ramp/Soak Step; Bit 24=Local Sensor Failover Permitted; Bit 25=Network Sensor Failover Permitted; Bit 26-30=Spare; Bit 31=Setpoint Failover Active | <enumeration> | See Modbus_Status sheet for details (byte enumeration and bit-packed).
| TRUE | STATUS | w_NET_Sts_TemperatureState |  | w_NET_Status_TemperatureState | Bit/Byte-packed enumerated status double-word: Bit 0=Machine has nearly achieved setpoint; Bit1=Machine has closely maintained setpoint; Bit 2=Machine is in steady-state; Bit 3=Machine is neither heating nor cooling; Bit 4=Machine is heating; Bit 5=Machine is cooling via solenoid or modulating valve; Bit 6=Machine is increasing cooling via floating valve; Bit 7=Machine is decreasing cooling via floating valve; Bit 8=Machine heat/cool is running in external hardwire control mode; Bits 9-23=Spare; Bits 24-21 Heating/Cooling Percent as an unsinged byte integer. | <enumeration> | See Modbus_Status sheet for details (bit-packed, and byte value).
| TRUE | STATUS | w_NET_Sts_AlarmMap1 |  | w_NET_Status_AlarmMap1 | Bit-packed status double-word: Bit 0=Spare; Bit 1=HMI Connection Failure; Bit 2=IO Module Link Failure; Bit 3=IO Module Hardware Mismatch; Bit 4=IO Module Internal Failure; Bit 5=IO Point Failure; Bit 6=Power Supply Voltage Low; Bit 7=Logic Supply Voltage Low; Bit 8=Overtemperature; Bit 9=Heater Contactor Stuck Closed; Bit 10=High Temperature - Factory Limit; Bit 11=Unbranded; Bit 12=Options Not Set; Bit 13=Phase Monitor; Bit 14=Pump Contactor Stuck Closed; Bit 15=Heater Contactor Stuck Open; Bit 16=Pump Contactor Stuck Open; Bit 17=Pressure Too High; Bit 18=Electrical Panel Too Hot; Bit 19=Low Temperature - Factory Limit; Bit 20=Brownout Occurred; Bit 21=High Temperature - User Limit; Bit 22=Temperature Low - User Limit; Bit 23=Low Pressure Standby Timeout; Bit 24=Low Pressure Strikeout; Bit 25=Pump Overload; Bit 26=Flowmeter Low Flow; Bit 27=Supply RTD - Open Circuit; Bit 28=Supply RTD -Short Circuit; Bit 29=Supply RTD - Channel Error; Bit 30=Return RTD - Open Circuit; Bit 31=Return RTD - Short Circuit. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_Sts_AlarmMap2 |  | w_NET_Status_AlarmMap2 | Bit-packed status double-word: Bit 0=Spare; Bit 1=Spare; Bit 2=Spare; Bit 3=Spare; Bit 4=Spare; Bit 5=Spare; Bit 6=Spare; Bit 7=Spare; Bit 8=Spare; Bit 9=Spare; Bit 10=Spare; Bit 11=Spare; Bit 12=Spare; Bit 13=Spare; Bit 14=Spare; Bit 15=Spare; Bit 16=Spare; Bit 17=Spare; Bit 18=Spare; Bit 19=Spare; Bit 20=Spare; Bit 21=Spare; Bit 22=Spare; Bit 23=Spare; Bit 24=Spare; Bit 25=Spare; Bit 26=Spare; Bit 27=Spare; Bit 28=Spare; Bit 29=Spare; Bit 30=Spare; Bit 31=Spare. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_Sts_AlarmMap3 |  | w_NET_Status_AlarmMap3 | Bit-packed status double-word: Bit 0=PID Autotune Failed, Starting Control Output Too High; Bit 1=PID Autotune Failed, Process Response Too Slow; Bit 2=PID Autotune Failed, Time Constant Not Found; Bit 3=PID Autotune Failed, Process Limit Exceeded; Bit 4=Spare; Bit 5=Spare; Bit 6=Spare; Bit 7=Spare; Bit 8=Spare; Bit 9=Spare; Bit 10=Spare; Bit 11=Spare; Bit 12=Spare; Bit 13=Spare; Bit 14=Spare; Bit 15=Spare; Bit 16=Spare; Bit 17=Spare; Bit 18=Spare; Bit 19=Spare; Bit 20=Spare; Bit 21=Spare; Bit 22=Spare; Bit 23=Spare; Bit 24=Spare; Bit 25=Spare; Bit 26=Spare; Bit 27=Spare; Bit 28=Spare; Bit 29=Spare; Bit 30=Spare; Bit 31=Spare. | N/A | See Modbus_Status sheet for details (bit-packed).
| FALSE | STATUS | w_NET_Sts_AlarmMap4 |  | w_NET_Status_AlarmMap4 | Bit-packed status double-word: Bit 0=Spare; Bit 1=Spare; Bit 2=Spare; Bit 3=Spare; Bit 4=Spare; Bit 5=Spare; Bit 6=Spare; Bit 7=Spare; Bit 8=Spare; Bit 9=Spare; Bit 10=Spare; Bit 11=Spare; Bit 12=Spare; Bit 13=Spare; Bit 14=Spare; Bit 15=Spare; Bit 16=Spare; Bit 17=Spare; Bit 18=Spare; Bit 19=Spare; Bit 20=Spare; Bit 21=Spare; Bit 22=Spare; Bit 23=Spare; Bit 24=Spare; Bit 25=Spare; Bit 26=Spare; Bit 27=Spare; Bit 28=Spare; Bit 29=Spare; Bit 30=Spare; Bit 31=Spare. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_Sts_WarningAlarm |  | w_NET_Status_WarningAlarm | See Modbus_Status sheet for details (byte-packed). | N/A | See Modbus_Status sheet for details (byte-packed).
| TRUE | STATUS | w_NET_Sts_WarningMap1 |  | w_NET_Status_WarningMap1 | Bit-packed status double-word: Bit 0=Spare; Bit 1=Pump Overload; Bit 2=Flowmeter - Low Flow; Bit 3=Failover Active: Supply RTD --> Return RTD, due to Supply RTD - Open circuit; Bit 4=Failover Active: Supply RTD --> Return RTD, due to Supply RTD - Short circuit; Bit 5=Failover Active: Supply RTD --> Return RTD, due to Supply RTD - Channel error; Bit 6=Failover Active: Return RTD --> Supply RTD, due to Return RTD - Open circuit; Bit 7=Failover Active: Return RTD --> Supply RTD, due to Return RTD - Short circuit; Bit 8=Failover Active: Return RTD --> SupplyRTD, due to Return RTD - Channel error; Bit 9=Failover Active: Remote RTD --> Return RTD, due to Remote RTD - Open circuit; Bit 10=Failover Active: Remote RTD --> Return RTD, due to Remote RTD - Short circuit; Bit 11=Failover Active: Remote RTD --> Return RTD, due to Remote RTD - Channel error; Bit 12=Failover Active: Analog Process Input --> Return RTD, due to Analog Process Input - Signal high; Bit 13=Failover Active: Analog Process Input --> Return RTD, due to Analog Process Input - Signal low; Bit 14=Failover Active: Analog Process Input --> Return RTD, due to Analog Process Input - Channel error; Bit 15=Failover Active: Network Process Temperature --> Return RTD, due to Network Process Temperature - Signal high; Bit 16=Failover Active: Network Process Temperature --> Return RTD, due to Network Process Temperature - Signal low; Bit 17=Failover Active: Network Process Temperature --> Return RTD, due to Network Process Temperature - Heartbeat lost; Bit 18=Failover Active: Analog Setpoint Input --> Main Setpoint, due to Analog Setpoint - Signal high; Bit 19=Failover Active: Analog Setpoint Input --> Main Setpoint, due to Analog Setpoint - Signal low; Bit 20=Failover Active: Analog Setpoint Input --> Main Setpoint, due to Analog Setpoint - Channel error; Bit 21=Failover Active: Network Setpoint --> Main Setpoint, due to Network Setpoint - Signal high; Bit 22=Failover Active: Network Setpoint --> Main Setpoint, due to Network Setpoint - Signal low; Bit 23=Failover Active: Network Setpoint --> Main Setpoint, due to Network Setpoint - Heartbeat lost; Bit 24=System Pressure Below Minimum; Bit 25=System Pressure Not High Enough; Bit 26=Setpoint Too High For Pressure; Bit 27=Supply Transducer - Signal High; Bit 28=Supply Transducer - Signal Low; Bit 29=Supply Transducer - Channel Error; Bit 30=Supply RTD - Open circuit; Bit 31=Supply RTD - Short circuit. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_Sts_WarningMap2 |  | w_NET_Status_WarningMap2 | Bit-packed status double-word: Bit 0=Supply RTD - Channel error; Bit 1=Return RTD - Open circuit; Bit 2=Return RTD - Short circuit; Bit 3=Return RTD - Channel error; Bit 4=Analog Flowmeter - Signal High; Bit 5=Analog Flowmeter- Signal Low; Bit 6=Analog Flowmeter - Channel Error; Bit 7=Too Many Flash Memory Writes; Bit 8=High Temperature Deviation; Bit 9=Low Temperature Deviation; Bit 10=Network Heartbeat Lost; Bit 11=Remote Slave Warning Active; Bit 12=Too Frequent Heater Cycles; Bit 13=Worn Out Heater Contactor; Bit 14=Clock Not Set; Bit 15=Spare; Bit 16=Spare; Bit 17=Spare; Bit 18=Spare; Bit 19=Spare; Bit 20=Spare; Bit 21=Spare; Bit 22=Spare; Bit 23=Spare; Bit 24=Spare; Bit 25=Spare; Bit 26=Spare; Bit 27=Spare; Bit 28=Spare; Bit 29=Spare; Bit 30=Spare; Bit 31=Spare. | N/A | See Modbus_Status sheet for details (bit-packed).
| FALSE | STATUS | w_NET_Sts_WarningMap3 |  | w_NET_Status_WarningMap3 | Bit-packed status double-word: Bit 0=Spare; Bit 1=Spare; Bit 2=Spare; Bit 3=Spare; Bit 4=Spare; Bit 5=Spare; Bit 6=Spare; Bit 7=Spare; Bit 8=Spare; Bit 9=Spare; Bit 10=Spare; Bit 11=Spare; Bit 12=Spare; Bit 13=Spare; Bit 14=Spare; Bit 15=Spare; Bit 16=Spare; Bit 17=Spare; Bit 18=Spare; Bit 19=Spare; Bit 20=Spare; Bit 21=Spare; Bit 22=Spare; Bit 23=Spare; Bit 24=Spare; Bit 25=Spare; Bit 26=Spare; Bit 27=Spare; Bit 28=Spare; Bit 29=Spare; Bit 30=Spare; Bit 31=Spare. | N/A | See Modbus_Status sheet for details (bit-packed).
| FALSE | STATUS | w_NET_Sts_WarningMap4 |  | w_NET_Status_WarningMap4 | Bit-packed status double-word: Bit 0=Spare; Bit 1=Spare; Bit 2=Spare; Bit 3=Spare; Bit 4=Spare; Bit 5=Spare; Bit 6=Spare; Bit 7=Spare; Bit 8=Spare; Bit 9=Spare; Bit 10=Spare; Bit 11=Spare; Bit 12=Spare; Bit 13=Spare; Bit 14=Spare; Bit 15=Spare; Bit 16=Spare; Bit 17=Spare; Bit 18=Spare; Bit 19=Spare; Bit 20=Spare; Bit 21=Spare; Bit 22=Spare; Bit 23=Spare; Bit 24=Spare; Bit 25=Spare; Bit 26=Spare; Bit 27=Spare; Bit 28=Spare; Bit 29=Spare; Bit 30=Spare; Bit 31=Spare. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_IN_Value1 |  | w_NET_IN_Value1 | Bit-packed digital input status word: Bit 0=Phase Monitor; Bit 1=Pump Overload; Bit 2=Pump Contactor Aux; Bit 3=Heater Contactor Aux; Bit 4=Pressure Switch; Bit 5=Heater High Temp; Bit 6=Flow Switch; Bit 7=Remote Start; Bit 8=Setpoint Select Advance. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_OUT_Value1 |  | w_NET_OUT_Value1 | Bit-packed digital output status word: Bit 0=Alarm (Silenceable); Bit 1=Pump Contactor; Bit 2=Heater Contactor; Bit 3=Heater SSR; Bit 4=Alarm (Non-Silenceable); Bit 5=Mold Purge Solenoid Valves; Bit 6=Cooling Valve Open (Solenoid Valve only); Bit 7=Vent Solenoid Valve; Bit 8=Fill Valve. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_IN_Error1 |  | w_NET_IN_Error1 | Bit-packed digital input error word: Bit 0=Phase Monitor Input Error; Bit 1=Pump Overload Input Error; Bit 2=Pump Contactor Aux Input Error; Bit 3=Heater Contactor Aux Input Error; Bit 4=Pressure Switch Input Error; Bit 5=Heater High Temp Input Error; Bit 6=Flow Switch Input Error; Bit 7=Remote Start Input Error; Bit 8=Setpoint Select Advance Input Error. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_OUT_Error1 |  | w_NET_OUT_Error1 | Bit-packed digital output error word: Bit 0=Alarm (Silenceable) Output Error; Bit 1=Pump Contactor Output Error; Bit 2=Heater Contactor Output Error; Bit 3=Heater SSR Output Error; Bit 4=Alarm (Non-Silenceable) Output Error; Bit 5=Mold Purge Solenoid Valves Output Error; Bit 6=Cooling Valve Open Output Error (Solenoid Valve only); Bit 7=Vent Solenoid Valve Output Error; Bit 8=Fill Valve Output Error. | N/A | See Modbus_Status sheet for details (bit-packed).
| TRUE | STATUS | w_NET_Signal_Error1 |  | w_NET_Signal_Error1 | Nibble-packed enumerated analog output error double-word: Bits 0-3=To Process (Supply) Temperature RTD Error; Bits 4-7=From Process (Return) Temperature RTD Error; Bits 8-11=Remote Temperature RTD Error; Bits 12-15=Analog Process Temperature Error; Bits 16-19=Network Process Temperature Error; Bits 20-23=Analog Setpoint Error; Bits 24-27=Network Setpoint Error; Bits 28-31=To Process (Supply) Pressure Transducer Error. Enumeration for all: 0=Ok; 1=Circuit Open (RTD signals only); 2=Circuit Shorted (RTD signals only); 3=Error; 4=Not Used; 5=High Circuit (analog and network signals only); 6=Low Circuit (analog and network signals only); 7=Heartbeat Error (analog and network signals only) | N/A | See Modbus_Status sheet for details (nibble-packed).
| TRUE | STATUS | w_NET_Signal_Error2 |  | w_NET_Signal_Error2 | Nibble-packed enumerated analog output error double-word: Bits 0-3=From Process (Return) Pressure Transducer Error; Bits 4-7=Flowmeter Error; Bits 8-31=Spare. Enumeration for all: 0=Ok; 1=Circuit Open (RTD signals only); 2=Circuit Shorted (RTD signals only); 3=Error; 4=Not Used; 5=High Circuit (analog and network signals only); 6=Low Circuit (analog and network signals only); 7=Heartbeat Error (analog and network signals only) | N/A | See Modbus_Status sheet for details (nibble-packed).
| TRUE | STATUS | r_IN_SupplyRTD_Smoothed | 2 | r_IN_SupplyRTD_Smoothed | Temperature of the Supply (To Process) RTD, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C | Internally computed values.
| TRUE | STATUS | r_IN_ReturnRTD_Smoothed | 2 | r_IN_ReturnRTD_Smoothed | Tempertaure of the Return (From Process) RTD, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C | Internally computed values.
| TRUE | STATUS | r_SupplyReturnRTD_AvgSmoothed | 2 | r_SupplyReturnRTD_AvgSmoothed | Average of the tempertaure of the Supply/Return (To/From Process) RTDs, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C | Internally computed values.
| TRUE | STATUS | r_IN_RemoteRTD_Smoothed | 2 | r_IN_RemoteRTD_Smoothed | Tempertaure of the Remote RTD, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. | °C | Internally computed values.
| TRUE | STATUS | r_IN_AnalogProcessSmoothed | 2 | r_IN_AnalogProcessSmoothed | Tempertaure of an extrernal process temperature signal, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. Not yet implemented. | °C | Internally computed values.
| TRUE | STATUS | r_NET_ProcValueTempSmoothed | 2 | r_NET_ProcValueTempSmoothed | Tempertaure of a network-provided process temperature signal, smoothed with the display running average. Smootthing only occurs when unit is running. In units of °C. Not yet implemented. | °C | Internally computed values.
| TRUE | STATUS | r_IN_SupplyPressureSmoothed | 13 | r_IN_SupplyPressureSmoothed | Pressure measured by the Supply (To Process) transducer, smoothed with the display running average. Smootthing only occurs when unit is running. In units of psi. | psi | Internally computed values.
| TRUE | STATUS | r_IN_ReturnPressureSmoothed | 13 | r_IN_ReturnPressureSmoothed | Pressure measured by the Return (From Process) transducer, smoothed with the display running average. Smootthing only occurs when unit is running. In units of psi. | psi | Internally computed values.
| TRUE | STATUS | r_EffectiveProcessValue | 2 | r_EffectiveProcessValue | The raw process value which is being utilized internally by the control loop. Not smoothed. In units of °C. | °C | Internally computed values.
| TRUE | STATUS | r_FilteredEffectiveProcessValue | 2 | r_FilteredEffectiveProcessValue | The actual process value which is being utilized internally by the control loop, with filtering and smoothing applied. Smoothing only occurs when the unit is running. In units of °C. | °C | Internally computed values.
| TRUE | STATUS | r_EffectiveSetpointValue | 2 | r_EffectiveSetpointValue | The actual setpoint that is being utilized internally by the control loop. In units of °C. | °C | Internally computed values.
| TRUE | STATUS | r_EstimatedFlowrate | 5 | r_EstimatedFlowrate | The estimated flowrate in the system. In units of gpm. | gpm | Internally computed values.
| TRUE | STATUS | r_IN_SupplyRTD.Value | 2 | r_IN_SupplyRTD.Value | Temperature of the Supply (To Process) RTD. No smoothing is applied. In units of °C. | °C | Raw analog values.
| TRUE | STATUS | r_IN_ReturnRTD.Value | 2 | r_IN_ReturnRTD.Value | Tempertaure of the Return (From Process) RTD. No smoothing is applied. In units of °C. | °C | Raw analog values.
| TRUE | STATUS | r_SupplyReturnRTD_Avg | 2 | r_SupplyReturnRTD_Avg | Average of the tempertaure of the Supply/Return (To/From Process) RTDs. No smoothing is applied. In units of °C. | °C | Raw analog values.
| TRUE | STATUS | r_IN_RemoteRTD.Value | 2 | r_IN_RemoteRTD.Value | Tempertaure of the Remote RTD. In units of °C. No smoothing is applied. | °C | Raw analog values.
| TRUE | STATUS | r_IN_AnalogProcess.Value | 2 | r_IN_AnalogProcess.Value | Tempertaure of an extrernal process temperature signal. In units of °C. Not yet implemented. | °C | Raw analog values.
| TRUE | STATUS | r_IN_AnalogSetpoint.Value | 2 | r_IN_AnalogSetpoint.Value | Setpoint determined by an external analog signal. In units of °C. Not yet implemented. | °C | Raw analog values.
| TRUE | STATUS | r_IN_SupplyPressure.Value | 13 | r_IN_SupplyPressure.Value | Pressure measured by the Supply (To Process) transducer. No smoothing is applied. In units of psi. | psi | Raw analog values.
| TRUE | STATUS | r_IN_ReturnPressure.Value | 13 | r_IN_ReturnPressure.Value | Pressure measured by the Return (From Process) transducer. No smoothing is applied. In units of psi. | psi | Raw analog values.
| TRUE | STATUS | r_IN_AnalogFlowmeter.Value | 5 | r_IN_AnalogFlowmeter.Value | Flow measured by an analog flow meter. In units of gpm. | gpm | Raw analog values.
| TRUE | STATUS | r_IN_PulseFlowmeter.Value | 5 | r_IN_PulseFlowmeter.Value | Flow measured by a pulse flow meter. Smoothing is applied. In units of gpm. | gpm | Raw analog values.
| TRUE | STATUS | n_RampSoakActiveStep |  | n_RampSoakActiveStep | The active step in the ramp/soak profile. | N/A
| TRUE | STATUS | r_Flowmeter_Flowrate | 5 | r_Flowmeter_Flowrate | The flowrate measured by the flowmeter (pulse, analog or limit switch). If limit switch, it will be shown as 0.0 (low/bad flow) or 1.0 (flow). Otherwise, in units of gpm. | gpm
| TRUE | STATUS | n_LowPressureStrikeCount | 28 | n_LowPressureStrikeCount | The number of low pressure pause events which could contribute to an eventual shutdown if more continue to occur. | events
| TRUE | STATUS | r_NET_CoolingWaterTemperature | 2 | r_NET_CoolingWaterTemperature | The temperature of the cooling water, as measured at the end of the valve vent. In units of °C. | °C
| TRUE | STATUS | r_HotPressureNextReleaseTemp | 2 | r_HotPressureNextReleaseTemp | The temperature at which the next hot pressure release will occur. Only valid when using temperature-based pressure relief, otherwise 0 when using pressure-based pressure relief. In units of °C. | °C
| TRUE | STATUS | n_PID_SteadyStateTime | 8 | n_PID_SteadyStateTime | How long the unit has detected a continuous steady-state condition. In units of seconds. | seconds
| TRUE | STATUS | r_ActiveHeatToCoolOutRatio |  | r_ActiveHeatToCoolOutRatio | The current ratio of heating strength vs cooling strength on the PID loop output. | N/A
| TRUE | STATUS | b_EstimatedFlowrateValid | 31 | b_EstimatedFlowrateValid | Internally computed values. | Yes/No | Internally computed values.
| TRUE | STATUS | b_WarningActive | 31 | b_WarningActive | High if any warnings active. | Yes/No | High if any warnings active.
| TRUE | STATUS | b_AlarmActive | 31 | b_AlarmActive | High if any alarms active. | Yes/No | High if any alarms active.
| TRUE | STATUS | b_EnableRampSoak | 31 | b_EnableRampSoak | Enumerated value: FALSE=Ramp/Soak Disabled; TRUE=Ramp/Soak Enabled; | Yes/No | Bulky
| TRUE | STATUS | b_PAR_TempUnits.CurrentValue |  | b_PAR_TemperatureUnits.CurrentValue | Enumerated value: FALSE=Fahrenheit; TRUE=Celsius. | <enumeration> | Bulky
| TRUE | STATUS | b_PAR_FlowUnits.CurrentValue |  | b_PAR_FlowUnits.CurrentValue | Enumerated value: FALSE=Gallons; TRUE=Liters. | <enumeration> | Bulky
| TRUE | STATUS | b_PAR_PressureUnits.CurrentValue |  | b_PAR_PressureUnits.CurrentValue | Enumerated value: FALSE=psi; TRUE=bar. | <enumeration> | Bulky
Parameters
| TRUE | PARAMS_DINT | n_PAR_TCU_Type |  | n_PAR_TCU_Type | Product Name enumeration: 0=Unbranded; 1=Conair TW-B; 2=Conair TW-E; 3=Conair TW-T; 4=Thermal Care RQT Standard; 5=Thermal Care RQT Advanced; 6=Thermal Care RQT Premium
| TRUE | PARAMS_DINT | n_PAR_TCU_Type.CurrentValue |  | n_PAR_TCU_Type.CurrentValue | Brand and model of this unit. Enumerated value: IF b_PAR_OEM_Product.CurrentValue=FALSE: 0="Unbranded"; 1="Conair TW-B"; 2="Conair TW-E"; 3="Conair TW-T"; 4="TC RQT Std"; 5="TC RQT Adv"; 6="TC RQT Prem"; IF b_PAR_OEM_Product.CurrentValue=TRUE: 0="Unbranded"; 1="Type C Low"; 2="Type C Mid"; 3="Type C HIgh"; 4="Type T Low"; 5="Type T Mid"; 6="Type T High". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_TCU_Type.Implemented | 31 | n_PAR_TCU_Type.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No | Parameter .CurrentValue is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_TCU_Type.Maximum |  | n_PAR_TCU_Type.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration> | The maximum permitted value of .CurrentValue or .RemoteValue
| TRUE | PARAMS_DINT | n_PAR_TCU_Type.Minimum |  | n_PAR_TCU_Type.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration> | The minimum permitted value of .CurrentValue or .RemoteValue
| TRUE | PARAMS_DINT | n_PAR_TCU_Type.RemoteWriteAccess | 31 | n_PAR_TCU_Type.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_TCU_Type.RemoteValue |  | n_PAR_TCU_Type.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_MoldPurgeInstalled |  | b_PAR_MoldPurgeInstalled | Mold Purge enumeration: TRUE=Mold Purge Included; FALSE=No Mold Purge
| TRUE | PARAMS_BOOL | b_PAR_MoldPurgeInstalled.CurrentValue |  | b_PAR_MoldPurgeInstalled.CurrentValue | Tells the controller if mold purge plumbing is installed. Enumerated value: FALSE="Mold Purge" option not installed; TRUE="Mold Purge" option installed. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_MoldPurgeInstalled.Implemented | 31 | b_PAR_MoldPurgeInstalled.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_MoldPurgeInstalled.RemoteWriteAccess | 31 | b_PAR_MoldPurgeInstalled.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_MoldPurgeInstalled.RemoteValue | 31 | b_PAR_MoldPurgeInstalled.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_PhaseMonitorInstalled |  | b_PAR_PhaseMonitorInstalled | Phase Detection enumeration: FALSE=Phase monitor not installed; TRUE=Phase monitor is installed.
| TRUE | PARAMS_BOOL | b_PAR_PhaseMonitorInstalled.CurrentValue |  | b_PAR_PhaseMonitorInstalled.CurrentValue | Tells the controller if phase detection hardware is installed. Enumerated value: FALSE="Phase Monitor" not installed; TRUE="Phase Monitor" is installed. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_PhaseMonitorInstalled.Implemented | 31 | b_PAR_PhaseMonitorInstalled.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_PhaseMonitorInstalled.RemoteWriteAccess | 31 | b_PAR_PhaseMonitorInstalled.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_PhaseMonitorInstalled.RemoteValue | 31 | b_PAR_PhaseMonitorInstalled.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeaterControlType |  | n_PAR_HeaterControlType | Heater Contactor enumeration: 0=No heat (no feedback); 1=Mechanical Contactor (with feedback); 2=SSR (with feedback); 3=Mercury Contactor (no feedback)
| TRUE | PARAMS_DINT | n_PAR_HeaterControlType.CurrentValue |  | n_PAR_HeaterControlType.CurrentValue | Type of heater switching device and whether or not monitoring contacts provide feedback to the controller regarding contactor state. Enumerated value: 0="No Heat"; 1="E-Mech Contactor"; 2="SSR"; 3="Mercury". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeaterControlType.Implemented | 31 | n_PAR_HeaterControlType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HeaterControlType.Maximum |  | n_PAR_HeaterControlType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeaterControlType.Minimum |  | n_PAR_HeaterControlType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeaterControlType.RemoteWriteAccess | 31 | n_PAR_HeaterControlType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HeaterControlType.RemoteValue |  | n_PAR_HeaterControlType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpVoltageFreq |  | n_PAR_PumpVoltageFrequency | Voltage/Freq enumeration: 0=Not Selected; 1=460V/60Hz; 1=208V/60Hz; 3=230V/60Hz; 4=380V/60Hz; 5=400V/50Hz; 6=575V/60Hz
| TRUE | PARAMS_DINT | n_PAR_PumpVoltageFreq.CurrentValue |  | n_PAR_PumpVoltageFrequency.CurrentValue | Selects the installed pump voltage and frequency. Enumerated value: 0="Not Selected"; 1="460 V / 60 Hz"; 2="208 V / 60 Hz"; 3="230 V / 60 Hz"; 4="380 V / 60Hz"; 5="400 V / 50 Hz"; 6="575 V / 60 Hz". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpVoltageFreq.Implemented | 31 | n_PAR_PumpVoltageFrequency.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_PumpVoltageFreq.Maximum |  | n_PAR_PumpVoltageFrequency.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_PumpVoltageFreq.Minimum |  | n_PAR_PumpVoltageFrequency.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_PumpVoltageFreq.RemoteWriteAccess | 31 | n_PAR_PumpVoltageFrequency.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_PumpVoltageFreq.RemoteValue |  | n_PAR_PumpVoltageFrequency.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpHP |  | n_PAR_PumpHorsepower | Pump Size enumeration: 0=Not Selected; 1=0.5HP; 2=0.75HP; 3=1HP; 4=2HP; 5=3HP; 6=5HP; 7=7.5HP; 8=10HP (0.5HP is not currently available; 10HP only available for 60Hz)
| TRUE | PARAMS_DINT | n_PAR_PumpHP.CurrentValue |  | n_PAR_PumpHorsepower.CurrentValue | Selects the nominal horsepower of the pump. Enumerated value: 0="Not Selected"; 1="0.5 HP"; 2="0.75 HP"; 3="1 HP"; 4="2 HP"; 5="3 HP"; 6="5 HP"; 7="7.5 HP"; 8="10 HP". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpHP.Implemented | 31 | n_PAR_PumpHorsepower.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_PumpHP.Maximum |  | n_PAR_PumpHorsepower.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_PumpHP.Minimum |  | n_PAR_PumpHorsepower.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_PumpHP.RemoteWriteAccess | 31 | n_PAR_PumpHorsepower.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_PumpHP.RemoteValue |  | n_PAR_PumpHorsepower.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeaterKW |  | n_PAR_HeaterKilowats | Heater Size enumeration: 0=0kW; 1=9kW; 2=12kW; 3=18kW; 4=24kW; 5=36kW; or 6=48kW
| TRUE | PARAMS_DINT | n_PAR_HeaterKW.CurrentValue |  | n_PAR_HeaterKilowats.CurrentValue | Selects the installed heater size. Enumerated value: 0="None"; 1="9 kW"; 2="12 kW"; 3="18 kW"; 4="24 kW"; 5="36 kW"; or 6="48 kW". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeaterKW.Implemented | 31 | n_PAR_HeaterKilowats.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HeaterKW.Maximum |  | n_PAR_HeaterKilowats.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeaterKW.Minimum |  | n_PAR_HeaterKilowats.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeaterKW.RemoteWriteAccess | 31 | n_PAR_HeaterKilowats.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HeaterKW.RemoteValue |  | n_PAR_HeaterKilowats.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ReturnHardware |  | n_PAR_ReturnHardware | Return Circuit Type enumeration: 0=Mixing Tank; 1=Standard Performance Heat Exchanger; 2=High Performance Heat Exchanger; 3=Heater
| TRUE | PARAMS_DINT | n_PAR_ReturnHardware.CurrentValue |  | n_PAR_ReturnHardware.CurrentValue | Selects the installed hardware on the "From Process" side of the pump. Enumerated value: 0="Mixing Tank"; 1="Std Perf Heat Ex"; 2="High Perf Heat Ex"; 3="Heater". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ReturnHardware.Implemented | 31 | n_PAR_ReturnHardware.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_ReturnHardware.Maximum |  | n_PAR_ReturnHardware.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ReturnHardware.Minimum |  | n_PAR_ReturnHardware.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ReturnHardware.RemoteWriteAccess | 31 | n_PAR_ReturnHardware.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_ReturnHardware.RemoteValue |  | n_PAR_ReturnHardware.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_MaxTempConfig |  | n_PAR_MaximumTempConfig | Max Temp Config enumeration: 0=250°F or 1=300°F
| TRUE | PARAMS_DINT | n_PAR_MaxTempConfig.CurrentValue |  | n_PAR_MaximumTempConfig.CurrentValue | Selects the hardware configuration for maximum process loop temperature Enumerated value: 0="250°F"; 1="300°F". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_MaxTempConfig.Implemented | 31 | n_PAR_MaximumTempConfig.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_MaxTempConfig.Maximum |  | n_PAR_MaximumTempConfig.Maximumimum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_MaxTempConfig.Minimum |  | n_PAR_MaximumTempConfig.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_MaxTempConfig.RemoteWriteAccess | 31 | n_PAR_MaximumTempConfig.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_MaxTempConfig.RemoteValue |  | n_PAR_MaximumTempConfig.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CoolingValveType |  | n_PAR_CoolingValveType | Cooling Valve Type enumeration: 0=None; 1=Solenoid; 2=Modulating; 3=Floating (not yet implemented).
| TRUE | PARAMS_DINT | n_PAR_CoolingValveType.CurrentValue |  | n_PAR_CoolingValveType.CurrentValue | Selects what kind of cooling valve is connected to the unit. Enumerated value: 0="None"; 1="Solenoid"; 2="Modulating"; 3="Floating" (not yet implemented). | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CoolingValveType.Implemented | 31 | n_PAR_CoolingValveType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_CoolingValveType.Maximum |  | n_PAR_CoolingValveType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_CoolingValveType.Minimum |  | n_PAR_CoolingValveType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_CoolingValveType.RemoteWriteAccess | 31 | n_PAR_CoolingValveType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_CoolingValveType.RemoteValue |  | n_PAR_CoolingValveType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ModCoolingValveCv |  | n_PAR_ModulatingCoolingValveCv | Modulating Cooling Valve Cv enumeration: 0=Not Selected, 1=1.2Cv, 2=2.9Cv, 3=4.7Cv, 4= 7.4Cv, 5=11.7Cv, 6=24Cv, 7=30Cv
| TRUE | PARAMS_DINT | n_PAR_ModCoolingValveCv.CurrentValue |  | n_PAR_ModulatingCoolingValveCv.CurrentValue | Specifies the Cv of the modulating cooling valve. (Cv=Number of gallons through the valve per minute at a 1psi pressure drop.) Enumerated value: 0="Not Selected", 1="1.2 Cv", 2="2.9 Cv", 3="4.7 Cv", 4= "7.4 Cv", 5="11.7 Cv", 6="24 Cv", 7="30 Cv". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ModCoolingValveCv.Implemented | 31 | n_PAR_ModulatingCoolingValveCv.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_ModCoolingValveCv.Maximum |  | n_PAR_ModulatingCoolingValveCv.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ModCoolingValveCv.Minimum |  | n_PAR_ModulatingCoolingValveCv.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ModCoolingValveCv.RemoteWriteAccess | 31 | n_PAR_ModulatingCoolingValveCv.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_ModCoolingValveCv.RemoteValue |  | n_PAR_ModulatingCoolingValveCv.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_DINT | n_PAR_SolCoolingValveCv |  | n_PAR_SolenoidCoolingValveCv | Solenoid Cooling Valve Cv enumeration: 0=Undetermined, 1=0.5Cv, 2=1.5Cv, 3=2.5Cv, 4=5.0Cv, 5=8.0Cv, 6=13.0Cv
| FALSE | PARAMS_DINT | n_PAR_SolCoolingValveCv.CurrentValue |  | n_PAR_SolenoidCoolingValveCv.CurrentValue | Not currently implemented. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| FALSE | PARAMS_DINT | n_PAR_SolCoolingValveCv.Implemented | 31 | n_PAR_SolenoidCoolingValveCv.Implemented | Not currently implemented. | Yes/No
| FALSE | PARAMS_DINT | n_PAR_SolCoolingValveCv.Maximum |  | n_PAR_SolenoidCoolingValveCv.Maximum | Not currently implemented. | <enumeration>
| FALSE | PARAMS_DINT | n_PAR_SolCoolingValveCv.Minimum |  | n_PAR_SolenoidCoolingValveCv.Minimum | Not currently implemented. | <enumeration>
| FALSE | PARAMS_DINT | n_PAR_SolCoolingValveCv.RemoteWriteAccess | 31 | n_PAR_SolenoidCoolingValveCv.RemoteWriteAccess | Not currently implemented. | Yes/No | Determines if values will be accepted from .RemoteValue.
| FALSE | PARAMS_DINT | n_PAR_SolCoolingValveCv.RemoteValue |  | n_PAR_SolenoidCoolingValveCv.RemoteValue | Not currently implemented. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CV_PressReliefDuration |  | n_PAR_CoolingValve_PressReliefDuration | How long to keep cooling valve open when performing an automatic hot pressure relief. In units of milliseconds (ms).
| TRUE | PARAMS_DINT | n_PAR_CV_PressReliefDuration.CurrentValue | 7 | n_PAR_CoolingValve_PressReliefDuration.CurrentValue | How long to keep cooling valve open when performing an automatic hot pressure relief. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CV_PressReliefDuration.Implemented | 31 | n_PAR_CoolingValve_PressReliefDuration.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_CV_PressReliefDuration.Maximum | 7 | n_PAR_CoolingValve_PressReliefDuration.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_CV_PressReliefDuration.Minimum | 7 | n_PAR_CoolingValve_PressReliefDuration.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_CV_PressReliefDuration.RemoteWriteAccess | 31 | n_PAR_CoolingValve_PressReliefDuration.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_CV_PressReliefDuration.RemoteValue | 7 | n_PAR_CoolingValve_PressReliefDuration.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CV_FullStrokeDuration |  | n_PAR_CoolingValve_FullStrokeDuration | Time for cooling valve to traverse from fully closed to fully open. In units of milliseconds (ms).
| TRUE | PARAMS_DINT | n_PAR_CV_FullStrokeDuration.CurrentValue | 7 | n_PAR_CoolingValve_FullStrokeDuration.CurrentValue | Time for cooling valve to traverse from fully closed to fully open. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CV_FullStrokeDuration.Implemented | 31 | n_PAR_CoolingValve_FullStrokeDuration.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_CV_FullStrokeDuration.Maximum | 7 | n_PAR_CoolingValve_FullStrokeDuration.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_CV_FullStrokeDuration.Minimum | 7 | n_PAR_CoolingValve_FullStrokeDuration.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_CV_FullStrokeDuration.RemoteWriteAccess | 31 | n_PAR_CoolingValve_FullStrokeDuration.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_CV_FullStrokeDuration.RemoteValue | 7 | n_PAR_CoolingValve_FullStrokeDuration.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMinPosition |  | r_PAR_CoolingValve_ValveMinimumPosition | Maximum cooling valve actuator position where the valve will have no flow. In units of %.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMinPosition.CurrentValue | 11 | r_PAR_CoolingValve_ValveMinimumPosition.CurrentValue | Maximum cooling valve actuator position where the valve will have no flow. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMinPosition.Implemented | 31 | r_PAR_CoolingValve_ValveMinimumPosition.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMinPosition.Maximum | 11 | r_PAR_CoolingValve_ValveMinimumPosition.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMinPosition.Minimum | 11 | r_PAR_CoolingValve_ValveMinimumPosition.Minimumimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMinPosition.RemoteWriteAccess | 31 | r_PAR_CoolingValve_ValveMinimumPosition.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMinPosition.RemoteValue | 11 | r_PAR_CoolingValve_ValveMinimumPosition.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMaxPosition |  | r_PAR_CoolingValve_ValveMaximumPosition | Minimum cooling valve actuator position where the valve will have full flow. In units of %.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMaxPosition.CurrentValue | 11 | r_PAR_CoolingValve_ValveMaximumPosition.CurrentValue | Minimum cooling valve actuator position where the valve will have full flow. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMaxPosition.Implemented | 31 | r_PAR_CoolingValve_ValveMaximumPosition.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMaxPosition.Maximum | 11 | r_PAR_CoolingValve_ValveMaximumPosition.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMaxPosition.Minimum | 11 | r_PAR_CoolingValve_ValveMaximumPosition.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMaxPosition.RemoteWriteAccess | 31 | r_PAR_CoolingValve_ValveMaximumPosition.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CV_ValveMaxPosition.RemoteValue | 11 | r_PAR_CoolingValve_ValveMaximumPosition.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_UtilizedRange |  | r_PAR_CoolingValve_UtilizedRange | Maximum cooling valve actuator position used to limit cooling. In units of %.
| TRUE | PARAMS_REAL | r_PAR_CV_UtilizedRange.CurrentValue | 11 | r_PAR_CoolingValve_UtilizedRange.CurrentValue | Maximum cooling valve actuator position used to limit cooling. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_UtilizedRange.Implemented | 31 | r_PAR_CoolingValve_UtilizedRange.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CV_UtilizedRange.Maximum | 11 | r_PAR_CoolingValve_UtilizedRange.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_UtilizedRange.Minimum | 11 | r_PAR_CoolingValve_UtilizedRange.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_UtilizedRange.RemoteWriteAccess | 31 | r_PAR_CoolingValve_UtilizedRange.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CV_UtilizedRange.RemoteValue | 11 | r_PAR_CoolingValve_UtilizedRange.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_PressureReliefOpenAmt |  | r_PAR_CoolingValve_PressureReliefOpenAmt | How far to open the cooling valve when performing an automatic hot pressure relief.
| TRUE | PARAMS_REAL | r_PAR_CV_PressureReliefOpenAmt.CurrentValue | 11 | r_PAR_CoolingValve_PressureReliefOpenAmt.CurrentValue | How far to open the cooling valve when performing an automatic hot pressure relief. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CV_PressureReliefOpenAmt.Implemented | 31 | r_PAR_CoolingValve_PressureReliefOpenAmt.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CV_PressureReliefOpenAmt.Maximum | 11 | r_PAR_CoolingValve_PressureReliefOpenAmt.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_PressureReliefOpenAmt.Minimum | 11 | r_PAR_CoolingValve_PressureReliefOpenAmt.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CV_PressureReliefOpenAmt.RemoteWriteAccess | 31 | r_PAR_CoolingValve_PressureReliefOpenAmt.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CV_PressureReliefOpenAmt.RemoteValue | 11 | r_PAR_CoolingValve_PressureReliefOpenAmt.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AnalogProcRetransmitType |  | n_PAR_AnalogProcessRetransmitType | Analog Proc Retransmit enumeration: 0=None; 1=4-20mA; 2=0-10V
| TRUE | PARAMS_DINT | n_PAR_AnalogProcRetransmitType.CurrentValue |  | n_PAR_AnalogProcessRetransmitType.CurrentValue | Analog input type for process temperature retransmit. Enumerated value: 0="None"; 1="4-20mA"; 2="0-10V". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AnalogProcRetransmitType.Implemented | 31 | n_PAR_AnalogProcessRetransmitType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_AnalogProcRetransmitType.Maximum |  | n_PAR_AnalogProcessRetransmitType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_AnalogProcRetransmitType.Minimum |  | n_PAR_AnalogProcessRetransmitType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_AnalogProcRetransmitType.RemoteWriteAccess | 31 | n_PAR_AnalogProcessRetransmitType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_AnalogProcRetransmitType.RemoteValue |  | n_PAR_AnalogProcessRetransmitType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_DINT | n_PAR_AnalogSetpointType |  | n_PAR_AnalogSetpointType | Setpoint Type enumeration: 0=None; 1=4-20mA; 2=0-10V
| FALSE | PARAMS_DINT | n_PAR_AnalogSetpointType.CurrentValue |  | n_PAR_AnalogSetpointType.CurrentValue | Not currently implemented. | <enumeration> | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogSetpointType.Implemented | 31 | n_PAR_AnalogSetpointType.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogSetpointType.Maximum |  | n_PAR_AnalogSetpointType.Maximum | Not currently implemented. | <enumeration> | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogSetpointType.Minimum |  | n_PAR_AnalogSetpointType.Minimum | Not currently implemented. | <enumeration> | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogSetpointType.RemoteWriteAccess | 31 | n_PAR_AnalogSetpointType.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogSetpointType.RemoteValue |  | n_PAR_AnalogSetpointType.RemoteValue | Not currently implemented. | <enumeration> | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogProcessInputType |  | n_PAR_AnalogProcessInputType | Process Value Input Type enumeration: 0=None; 1=4-20mA; 2=0-10V
| FALSE | PARAMS_DINT | n_PAR_AnalogProcessInputType.CurrentValue |  | n_PAR_AnalogProcessInputType.CurrentValue | Not currently implemented. | <enumeration> | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogProcessInputType.Implemented | 31 | n_PAR_AnalogProcessInputType.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogProcessInputType.Maximum |  | n_PAR_AnalogProcessInputType.Maximum | Not currently implemented. | <enumeration> | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogProcessInputType.Minimum |  | n_PAR_AnalogProcessInputType.Minimum | Not currently implemented. | <enumeration> | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogProcessInputType.RemoteWriteAccess | 31 | n_PAR_AnalogProcessInputType.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_AnalogProcessInputType.RemoteValue |  | n_PAR_AnalogProcessInputType.RemoteValue | Not currently implemented. | <enumeration> | Not currently implemented.
| TRUE | PARAMS_DINT | n_PAR_AutoLogoutTimeout |  | n_PAR_AutoLogoutTimeout | Duration of touchscreen inactivity before logged-in user reverts back to the default security level. In units of minutes (min).
| TRUE | PARAMS_DINT | n_PAR_AutoLogoutTimeout.CurrentValue | 9 | n_PAR_AutoLogoutTimeout.CurrentValue | Duration of touchscreen inactivity before logged-in user reverts back to the default security level. This is the current value for this parameter used in operation of the unit. | minutes | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AutoLogoutTimeout.Implemented | 31 | n_PAR_AutoLogoutTimeout.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_AutoLogoutTimeout.Maximum | 9 | n_PAR_AutoLogoutTimeout.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_AutoLogoutTimeout.Minimum | 9 | n_PAR_AutoLogoutTimeout.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_AutoLogoutTimeout.RemoteWriteAccess | 31 | n_PAR_AutoLogoutTimeout.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_AutoLogoutTimeout.RemoteValue | 9 | n_PAR_AutoLogoutTimeout.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterType |  | n_PAR_FlowmeterType | Type enumeration: 0=None; 1=Pulse rate; 2=Limit switch; 3=Analog 4-20mA; 4=Analog 0-10V
| TRUE | PARAMS_DINT | n_PAR_FlowmeterType.CurrentValue |  | n_PAR_FlowmeterType.CurrentValue | The type of flowmeter attached to the unit. Enumerated value: 0="None"; 1="Pulse Rate"; 2="Limit Switch"; 3="Analog 4-20mA"; 4="Analog 0-10V". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterType.Implemented | 31 | n_PAR_FlowmeterType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_FlowmeterType.Maximum |  | n_PAR_FlowmeterType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_FlowmeterType.Minimum |  | n_PAR_FlowmeterType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_FlowmeterType.RemoteWriteAccess | 31 | n_PAR_FlowmeterType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterType.RemoteValue |  | n_PAR_FlowmeterType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ReturnTransducerType |  | n_PAR_ReturnTransducerType | From Proc Sensor enumeration: 0=Switch; 1=Installed; 2=Bypass
| TRUE | PARAMS_DINT | n_PAR_ReturnTransducerType.CurrentValue |  | n_PAR_ReturnTransducerType.CurrentValue | Selects the From Process pressure transducer (or pressure switch) type. Enumerated value: 0="Switch"; 1="Installed"; 2="Bypass". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ReturnTransducerType.Implemented | 31 | n_PAR_ReturnTransducerType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_ReturnTransducerType.Maximum |  | n_PAR_ReturnTransducerType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ReturnTransducerType.Minimum |  | n_PAR_ReturnTransducerType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ReturnTransducerType.RemoteWriteAccess | 31 | n_PAR_ReturnTransducerType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_ReturnTransducerType.RemoteValue |  | n_PAR_ReturnTransducerType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_SupplyTransducerType |  | n_PAR_SupplyTransducerType | To Process Sensor enumeration: 0=None; 1=Installed
| TRUE | PARAMS_DINT | n_PAR_SupplyTransducerType.CurrentValue |  | n_PAR_SupplyTransducerType.CurrentValue | Selects the To Process pressure transducer type. Enumerated value: 0="None"; 1="Installed". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_SupplyTransducerType.Implemented | 31 | n_PAR_SupplyTransducerType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_SupplyTransducerType.Maximum |  | n_PAR_SupplyTransducerType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_SupplyTransducerType.Minimum |  | n_PAR_SupplyTransducerType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_SupplyTransducerType.RemoteWriteAccess | 31 | n_PAR_SupplyTransducerType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_SupplyTransducerType.RemoteValue |  | n_PAR_SupplyTransducerType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_Altitude |  | n_PAR_Altitude | Altitude at which the machine is installed, in order to properly calculate atmospheric pressure. In units of feet (ft).
| TRUE | PARAMS_DINT | n_PAR_Altitude.CurrentValue | 20 | n_PAR_Altitude.CurrentValue | Altitude at which the machine is installed, in order to properly calculate atmospheric pressure. This is the current value for this parameter used in operation of the unit. In units of ft. | ft | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_Altitude.Implemented | 31 | n_PAR_Altitude.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_Altitude.Maximum | 20 | n_PAR_Altitude.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | ft
| TRUE | PARAMS_DINT | n_PAR_Altitude.Minimum | 20 | n_PAR_Altitude.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | ft
| TRUE | PARAMS_DINT | n_PAR_Altitude.RemoteWriteAccess | 31 | n_PAR_Altitude.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_Altitude.RemoteValue | 20 | n_PAR_Altitude.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | ft | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_AMSP_BoilingMargin |  | r_PAR_AdaptiveMaximumSetpoint_BoilingMargin | How many degrees of margin are added to the boiling point calculation. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_AMSP_BoilingMargin.CurrentValue | 4 | r_PAR_AdaptiveMaximumSetpoint_BoilingMargin.CurrentValue | How many degrees of margin are added to the boiling point calculation. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_AMSP_BoilingMargin.Implemented | 31 | r_PAR_AdaptiveMaximumSetpoint_BoilingMargin.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_AMSP_BoilingMargin.Maximum | 4 | r_PAR_AdaptiveMaximumSetpoint_BoilingMargin.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_AMSP_BoilingMargin.Minimum | 4 | r_PAR_AdaptiveMaximumSetpoint_BoilingMargin.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_AMSP_BoilingMargin.RemoteWriteAccess | 31 | r_PAR_AdaptiveMaximumSetpoint_BoilingMargin.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_AMSP_BoilingMargin.RemoteValue | 4 | r_PAR_AdaptiveMaximumSetpoint_BoilingMargin.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_AlarmOutputReverseActing |  | b_PAR_AlarmOutputReverseActing | Non-Silenceable Alarm Output enumeration: FALSE=Non-sileanceable alarm output is active when alarm is active; TRUE=Non-sileanceable alarm output is active when alarm is NOT active.
| TRUE | PARAMS_BOOL | b_PAR_AlarmOutputReverseActing.CurrentValue |  | b_PAR_AlarmOutputReverseActing.CurrentValue | Flips the output behavior of the non-slienceable alarm output. Enumerated value: FALSE=Non-sileanceable alarm output is active when alarm is active; TRUE=Non-sileanceable alarm output is active when alarm is NOT active. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_AlarmOutputReverseActing.Implemented | 31 | b_PAR_AlarmOutputReverseActing.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_AlarmOutputReverseActing.RemoteWriteAccess | 31 | b_PAR_AlarmOutputReverseActing.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_AlarmOutputReverseActing.RemoteValue | 31 | b_PAR_AlarmOutputReverseActing.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MaxTempSetpoint |  | r_PAR_MaximumTempSetpoint | Maximum permitted setpoint for this machine, when operating at sufficient pressure. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_MaxTempSetpoint.CurrentValue | 2 | r_PAR_MaximumTempSetpoint.CurrentValue | Maximum permitted setpoint for this machine, when operating at sufficient pressure. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MaxTempSetpoint.Implemented | 31 | r_PAR_MaximumTempSetpoint.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_MaxTempSetpoint.Maximum | 2 | r_PAR_MaximumTempSetpoint.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MaxTempSetpoint.Minimum | 2 | r_PAR_MaximumTempSetpoint.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MaxTempSetpoint.RemoteWriteAccess | 31 | r_PAR_MaximumTempSetpoint.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_MaxTempSetpoint.RemoteValue | 2 | r_PAR_MaximumTempSetpoint.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MinTempSetpoint |  | r_PAR_MinimumTempSetpoint | Minimum permitted setpoint for this machine. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_MinTempSetpoint.CurrentValue | 2 | r_PAR_MinimumTempSetpoint.CurrentValue | Minimum permitted setpoint for this machine. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MinTempSetpoint.Implemented | 31 | r_PAR_MinimumTempSetpoint.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_MinTempSetpoint.Maximum | 2 | r_PAR_MinimumTempSetpoint.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MinTempSetpoint.Minimum | 2 | r_PAR_MinimumTempSetpoint.Minimumimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MinTempSetpoint.RemoteWriteAccess | 31 | r_PAR_MinimumTempSetpoint.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_MinTempSetpoint.RemoteValue | 2 | r_PAR_MinimumTempSetpoint.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MaxHeaterDutyCycle |  | r_PAR_MaximumHeaterDutyCycle | Maximum PWM duty cycle for the heater. This is the current value for this parameter used in operation of the unit. In units of %.
| TRUE | PARAMS_REAL | r_PAR_MaxHeaterDutyCycle.CurrentValue | 11 | r_PAR_MaximumHeaterDutyCycle.CurrentValue | Maximum PWM duty cycle for the heater. Can be used to limit heating or electrical amps. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MaxHeaterDutyCycle.Implemented | 31 | r_PAR_MaximumHeaterDutyCycle.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_MaxHeaterDutyCycle.Maximum | 11 | r_PAR_MaximumHeaterDutyCycle.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_MaxHeaterDutyCycle.Minimum | 11 | r_PAR_MaximumHeaterDutyCycle.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_MaxHeaterDutyCycle.RemoteWriteAccess | 31 | r_PAR_MaximumHeaterDutyCycle.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_MaxHeaterDutyCycle.RemoteValue | 11 | r_PAR_MaximumHeaterDutyCycle.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_SerialNumber |  | n_PAR_SerialNumber | Serial number of the machine.
| TRUE | PARAMS_DINT | n_PAR_SerialNumber.CurrentValue |  | n_PAR_SerialNumber.CurrentValue | Serial number of the machine. This is the current value for this parameter used in operation of the unit. | N/A | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_SerialNumber.Implemented | 31 | n_PAR_SerialNumber.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_SerialNumber.Maximum |  | n_PAR_SerialNumber.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | N/A
| TRUE | PARAMS_DINT | n_PAR_SerialNumber.Minimum |  | n_PAR_SerialNumber.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | N/A
| TRUE | PARAMS_DINT | n_PAR_SerialNumber.RemoteWriteAccess | 31 | n_PAR_SerialNumber.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_SerialNumber.RemoteValue |  | n_PAR_SerialNumber.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempHighAlarm |  | r_PAR_FactoryTemperatureHighAlarm | Process temperature at which a high temperature alarm will occur. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempHighAlarm.CurrentValue | 2 | r_PAR_FactoryTemperatureHighAlarm.CurrentValue | Process temperature at which a high temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempHighAlarm.Implemented | 31 | r_PAR_FactoryTemperatureHighAlarm.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_FactoryTempHighAlarm.Maximum | 2 | r_PAR_FactoryTemperatureHighAlarm.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_FactoryTempHighAlarm.Minimum | 2 | r_PAR_FactoryTemperatureHighAlarm.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_FactoryTempHighAlarm.RemoteWriteAccess | 31 | r_PAR_FactoryTemperatureHighAlarm.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempHighAlarm.RemoteValue | 2 | r_PAR_FactoryTemperatureHighAlarm.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempLowAlarm |  | r_PAR_FactoryTemperatureLowAlarm | Process temperature at which a low temperature alarm will occur. In units of degrees C.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempLowAlarm.CurrentValue | 2 | r_PAR_FactoryTemperatureLowAlarm.CurrentValue | Process temperature at which a low temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempLowAlarm.Implemented | 31 | r_PAR_FactoryTemperatureLowAlarm.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_FactoryTempLowAlarm.Maximum | 2 | r_PAR_FactoryTemperatureLowAlarm.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_FactoryTempLowAlarm.Minimum | 2 | r_PAR_FactoryTemperatureLowAlarm.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_FactoryTempLowAlarm.RemoteWriteAccess | 31 | r_PAR_FactoryTemperatureLowAlarm.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_FactoryTempLowAlarm.RemoteValue | 2 | r_PAR_FactoryTemperatureLowAlarm.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MinPressToRun |  | r_PAR_MinimumPressureToRun | Minimum pressure required to operate at low temperatures. In units of psi.
| TRUE | PARAMS_REAL | r_PAR_MinPressToRun.CurrentValue | 13 | r_PAR_MinimumPressureToRun.CurrentValue | Minimum pressure required to operate at low temperatures. This is the current value for this parameter used in operation of the unit. In units of psi. | psi | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MinPressToRun.Implemented | 31 | r_PAR_MinimumPressureToRun.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_MinPressToRun.Maximum | 13 | r_PAR_MinimumPressureToRun.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | psi
| TRUE | PARAMS_REAL | r_PAR_MinPressToRun.Minimum | 13 | r_PAR_MinimumPressureToRun.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | psi
| TRUE | PARAMS_REAL | r_PAR_MinPressToRun.RemoteWriteAccess | 31 | r_PAR_MinimumPressureToRun.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_MinPressToRun.RemoteValue | 13 | r_PAR_MinimumPressureToRun.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | psi | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_RemoteStartEnable |  | b_PAR_RemoteStartEnable | Remote Start enumeration: TRUE=Allow Remote Start; FALSE=Do Not Allow Remote Start
| TRUE | PARAMS_BOOL | b_PAR_RemoteStartEnable.CurrentValue |  | b_PAR_RemoteStartEnable.CurrentValue | Allows the unit to be started with an externally-switched digital input. Enumerated value: FALSE=Do not allow "Remote Start"; TRUE=Allow "Remote Start". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_RemoteStartEnable.Implemented | 31 | b_PAR_RemoteStartEnable.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_RemoteStartEnable.RemoteWriteAccess | 31 | b_PAR_RemoteStartEnable.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_RemoteStartEnable.RemoteValue | 31 | b_PAR_RemoteStartEnable.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_AutoRestartEnable |  | b_PAR_AutoRestartEnable | Auto Restart enumeration: TRUE=Allow Auto Restart; FALSE=Do Not Allow Auto Restart
| TRUE | PARAMS_BOOL | b_PAR_AutoRestartEnable.CurrentValue |  | b_PAR_AutoRestartEnable.CurrentValue | Causes the unit to automatically restart if power was lost while the unit was running. Enumerated value: FALSE=Do not allow "Auto Restart"; TRUE=Allow "Auto Restart". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_AutoRestartEnable.Implemented | 31 | b_PAR_AutoRestartEnable.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_AutoRestartEnable.RemoteWriteAccess | 31 | b_PAR_AutoRestartEnable.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_AutoRestartEnable.RemoteValue | 31 | b_PAR_AutoRestartEnable.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AutoRestartDelay |  | n_PAR_AutoRestartDelay | How long to wait before auto-restarting the machine once electrical power is restored. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_AutoRestartDelay.CurrentValue | 8 | n_PAR_AutoRestartDelay.CurrentValue | How long to wait before auto-restarting the machine once electrical power is restored. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AutoRestartDelay.Implemented | 31 | n_PAR_AutoRestartDelay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_AutoRestartDelay.Maximum | 8 | n_PAR_AutoRestartDelay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_AutoRestartDelay.Minimum | 8 | n_PAR_AutoRestartDelay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_AutoRestartDelay.RemoteWriteAccess | 31 | n_PAR_AutoRestartDelay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_AutoRestartDelay.RemoteValue | 8 | n_PAR_AutoRestartDelay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_BrownoutMonitorEnable |  | b_PAR_BrownoutMonitorEnable | Brownout Monitor enumeration: TRUE=Enable Brownout Monitor; FALSE=Do Not Monitor for Brownouts
| TRUE | PARAMS_BOOL | b_PAR_BrownoutMonitorEnable.CurrentValue |  | b_PAR_BrownoutMonitorEnable.CurrentValue | Causes the unit to alarm upon return of power if the unit was running when power was lost. Enumerated value: FALSE=Do not enable "Brownout Monitor"; TRUE=Enable "Brownout Monitor". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_BrownoutMonitorEnable.Implemented | 31 | b_PAR_BrownoutMonitorEnable.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_BrownoutMonitorEnable.RemoteWriteAccess | 31 | b_PAR_BrownoutMonitorEnable.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_BrownoutMonitorEnable.RemoteValue | 31 | b_PAR_BrownoutMonitorEnable.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_TempUnits |  | b_PAR_TemperatureUnits | Temperature Units enumeration: FALSE=Fahrenheit; TRUE=Celsius
| TRUE | PARAMS_BOOL | b_PAR_TempUnits.CurrentValue |  | b_PAR_TemperatureUnits.CurrentValue | Enumerated value: FALSE=Fahrenheit; TRUE=Celsius. | <enumeration> | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_TempUnits.Implemented | 31 | b_PAR_TemperatureUnits.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_TempUnits.RemoteWriteAccess | 31 | b_PAR_TemperatureUnits.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_TempUnits.RemoteValue | 31 | b_PAR_TemperatureUnits.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_FlowUnits |  | b_PAR_FlowUnits | Flow Units enumeration: FALSE=Gallons; TRUE=Liters
| TRUE | PARAMS_BOOL | b_PAR_FlowUnits.CurrentValue |  | b_PAR_FlowUnits.CurrentValue | Enumerated value: FALSE=Gallons; TRUE=Liters. | <enumeration> | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_FlowUnits.Implemented | 31 | b_PAR_FlowUnits.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_FlowUnits.RemoteWriteAccess | 31 | b_PAR_FlowUnits.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_FlowUnits.RemoteValue | 31 | b_PAR_FlowUnits.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_PressureUnits |  | b_PAR_PressureUnits | Pressure Units enumeration: FALSE=psi; TRUE=bar
| TRUE | PARAMS_BOOL | b_PAR_PressureUnits.CurrentValue |  | b_PAR_PressureUnits.CurrentValue | Enumerated value: FALSE=psi; TRUE=bar. | <enumeration> | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_PressureUnits.Implemented | 31 | b_PAR_PressureUnits.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_PressureUnits.RemoteWriteAccess | 31 | b_PAR_PressureUnits.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_BOOL | b_PAR_PressureUnits.RemoteValue | 31 | b_PAR_PressureUnits.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | Currently disabled and deferred to global units (n_PAR_GlobalUnits).
| TRUE | PARAMS_DINT | n_PAR_GlobalUnits |  | n_PAR_GlobalUnits | Units enumeration: 0=Custom, 1=English, 2=Metric.
| TRUE | PARAMS_DINT | n_PAR_GlobalUnits.CurrentValue |  | n_PAR_GlobalUnits.CurrentValue | Selects Imperial US or Metric units of measure for all numbers displayed on the touchscreen. Enumerated value: 0="Custom", 1="Imperial US", 2="Metric". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_GlobalUnits.Implemented | 31 | n_PAR_GlobalUnits.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_GlobalUnits.Maximum |  | n_PAR_GlobalUnits.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_GlobalUnits.Minimum |  | n_PAR_GlobalUnits.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_GlobalUnits.RemoteWriteAccess | 31 | n_PAR_GlobalUnits.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_GlobalUnits.RemoteValue |  | n_PAR_GlobalUnits.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BootupSecurityLevel |  | n_PAR_BootupSecurityLevel | Default Security Level enumeration: 0=Lowest; Others, see column header in this sheet.
| TRUE | PARAMS_DINT | n_PAR_BootupSecurityLevel.CurrentValue |  | n_PAR_BootupSecurityLevel.CurrentValue | The user level that will be defaultly logged in at bootup, or when an elevated user logs out. Enumerated value: 0="Guest"; 1="Operator"; 2="Setup"; 3="Service"; 4="Administrator". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BootupSecurityLevel.Implemented | 31 | n_PAR_BootupSecurityLevel.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_BootupSecurityLevel.Maximum |  | n_PAR_BootupSecurityLevel.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_BootupSecurityLevel.Minimum |  | n_PAR_BootupSecurityLevel.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_BootupSecurityLevel.RemoteWriteAccess | 31 | n_PAR_BootupSecurityLevel.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_BootupSecurityLevel.RemoteValue |  | n_PAR_BootupSecurityLevel.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BacklightTimeout |  | n_PAR_BacklightTimeout | Duration of touchscreen inactivity before the screen backlight is deenergized. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_BacklightTimeout.CurrentValue | 8 | n_PAR_BacklightTimeout.CurrentValue | Duration of touchscreen inactivity before the screen backlight is dimmed. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BacklightTimeout.Implemented | 31 | n_PAR_BacklightTimeout.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_BacklightTimeout.Maximum | 8 | n_PAR_BacklightTimeout.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_BacklightTimeout.Minimum | 8 | n_PAR_BacklightTimeout.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_BacklightTimeout.RemoteWriteAccess | 31 | n_PAR_BacklightTimeout.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_BacklightTimeout.RemoteValue | 8 | n_PAR_BacklightTimeout.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ScreenSaverTimeout |  | n_PAR_ScreenSaverTimeout | Duration of touchscreen inactivity before the screensaver is activated. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_ScreenSaverTimeout.CurrentValue | 8 | n_PAR_ScreenSaverTimeout.CurrentValue | Duration of touchscreen inactivity before the screensaver is activated. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ScreenSaverTimeout.Implemented | 31 | n_PAR_ScreenSaverTimeout.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_ScreenSaverTimeout.Maximum | 8 | n_PAR_ScreenSaverTimeout.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_ScreenSaverTimeout.Minimum | 8 | n_PAR_ScreenSaverTimeout.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_ScreenSaverTimeout.RemoteWriteAccess | 31 | n_PAR_ScreenSaverTimeout.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_ScreenSaverTimeout.RemoteValue | 8 | n_PAR_ScreenSaverTimeout.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Left |  | n_PAR_HomeScreenKPI_Left | Homescreen Left KPI enumeration: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate".
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Left.CurrentValue |  | n_PAR_HomeScreenKPI_Left.CurrentValue | Defines which KPI will be shown on the left space of the home screen. Enumerated value: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Left.Implemented | 31 | n_PAR_HomeScreenKPI_Left.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Left.Maximum |  | n_PAR_HomeScreenKPI_Left.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Left.Minimum |  | n_PAR_HomeScreenKPI_Left.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Left.RemoteWriteAccess | 31 | n_PAR_HomeScreenKPI_Left.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Left.RemoteValue |  | n_PAR_HomeScreenKPI_Left.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Right |  | n_PAR_HomeScreenKPI_Right | Homescreen Right KPI enumeration: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate".
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Right.CurrentValue |  | n_PAR_HomeScreenKPI_Right.CurrentValue | Defines which KPI will be shown on the right space of the home screen. Enumerated value: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Right.Implemented | 31 | n_PAR_HomeScreenKPI_Right.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Right.Maximum |  | n_PAR_HomeScreenKPI_Right.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Right.Minimum |  | n_PAR_HomeScreenKPI_Right.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Right.RemoteWriteAccess | 31 | n_PAR_HomeScreenKPI_Right.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Right.RemoteValue |  | n_PAR_HomeScreenKPI_Right.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Screensaver |  | n_PAR_HomeScreenKPI_Screensaver | Screen Saver KPI enumeration: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate".
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Screensaver.CurrentValue |  | n_PAR_HomeScreenKPI_Screensaver.CurrentValue | Defines which KPI will be shown on the screensaver. Enumerated value: 1="To Process Temp", 2="From Process Temp", 3="Remote Temp", 4="To/From Avg Temp", 5="Flow Rate", 6="To Process Press", 7="From Process Press", 8="Heat / Cool", 9="Active Process Temp", 10="Estimated Flow Rate". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Screensaver.Implemented | 31 | n_PAR_HomeScreenKPI_Screensaver.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Screensaver.Maximum |  | n_PAR_HomeScreenKPI_Screensaver.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Screensaver.Minimum |  | n_PAR_HomeScreenKPI_Screensaver.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Screensaver.RemoteWriteAccess | 31 | n_PAR_HomeScreenKPI_Screensaver.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HomeScreenKPI_Screensaver.RemoteValue |  | n_PAR_HomeScreenKPI_Screensaver.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_BOOL | b_PAR_DisplayFilteredPV |  | b_PAR_DisplayFilteredProcessValue | Filtered PV enumeration: TRUE=Display smoothed and dynamic deadbanded process value; FALSE=Display raw process value with no smoothing and no dynamic deadband.
| FALSE | PARAMS_BOOL | b_PAR_DisplayFilteredPV.CurrentValue |  | b_PAR_DisplayFilteredProcessValue.CurrentValue | Defines which KPI will be shown on the screensaver. Enumerated value: FALSE=Display raw process value with no smoothing and no dynamic deadband.; TRUE=Display smoothed and dynamic deadbanded process value. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| FALSE | PARAMS_BOOL | b_PAR_DisplayFilteredPV.Implemented | 31 | b_PAR_DisplayFilteredProcessValue.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| FALSE | PARAMS_BOOL | b_PAR_DisplayFilteredPV.RemoteWriteAccess | 31 | b_PAR_DisplayFilteredProcessValue.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| FALSE | PARAMS_BOOL | b_PAR_DisplayFilteredPV.RemoteValue | 31 | b_PAR_DisplayFilteredProcessValue.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HotPressReliefThreshold |  | n_PAR_HotPressReliefThreshold | Relief Trigger enumeration: 0=Disabled; 1=Auto; 2=2.77C(5F); 3=5.55C(10F); 4=8.33C(15F); 5=11.1C(20F); 6=13.8C(25F); 7=16.6C(30F); 8=22.2C(40F); 9=27.7C(50F); 10=38.8C(70F); 11=50.0C(90F); 12=61.1C(110F); 13=72.2C(130F); 14=83.3C(150F); 15=94.4C(170F); 16=111.1C(200F).
| TRUE | PARAMS_DINT | n_PAR_HotPressReliefThreshold.CurrentValue |  | n_PAR_HotPressReliefThreshold.CurrentValue | How many degrees in temperature rise should the unit wait before relieving process pressure as a result of thermal expansion. Enumerated value: 0="Disabled"; 1="Auto"; 2="5°F"/"2.78°C"; 3="10°F"/"5.56°C"; 4="15°F"/"8.33°C"; 5="20°F"/"11.1°C"; 6="25°F"/"13.8°C"; 7="30°F"/"16.6°C"; 8="40°F"/"22.2°C"; 9="50°F"/"27.7°C"; 10="70°F"/"38.8°C"; 11="90°F"/"50.0°C"; 12="110°F"/"61.1°C"; 13="130°F"/"72.2°C"; 14="150°F"/"83.3°C"; 15="170°F"/"94.4°C"; 16="200°F"/"111.1°C". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HotPressReliefThreshold.Implemented | 31 | n_PAR_HotPressReliefThreshold.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HotPressReliefThreshold.Maximum |  | n_PAR_HotPressReliefThreshold.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HotPressReliefThreshold.Minimum |  | n_PAR_HotPressReliefThreshold.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HotPressReliefThreshold.RemoteWriteAccess | 31 | n_PAR_HotPressReliefThreshold.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HotPressReliefThreshold.RemoteValue |  | n_PAR_HotPressReliefThreshold.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage1 |  | n_PAR_VentDurationStage1 | Duration of the vent cycle with only the cooling valve open (no pump). In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage1.CurrentValue | 8 | n_PAR_VentDurationStage1.CurrentValue | Duration of the vent cycle with only the cooling valve open (no pump). This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage1.Implemented | 31 | n_PAR_VentDurationStage1.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage1.Maximum | 8 | n_PAR_VentDurationStage1.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage1.Minimum | 8 | n_PAR_VentDurationStage1.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage1.RemoteWriteAccess | 31 | n_PAR_VentDurationStage1.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage1.RemoteValue | 8 | n_PAR_VentDurationStage1.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage2 |  | n_PAR_VentDurationStage2 | Duration of the vent cycle with both the cooling valve open and the pump running. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage2.CurrentValue | 8 | n_PAR_VentDurationStage2.CurrentValue | Duration of the vent cycle with both the cooling valve open and the pump running. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage2.Implemented | 31 | n_PAR_VentDurationStage2.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage2.Maximum | 8 | n_PAR_VentDurationStage2.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage2.Minimum | 8 | n_PAR_VentDurationStage2.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage2.RemoteWriteAccess | 31 | n_PAR_VentDurationStage2.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_VentDurationStage2.RemoteValue | 8 | n_PAR_VentDurationStage2.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_VentBypassTemp |  | r_PAR_VentBypassTemp | Process temperature above which the vent cycles will be skipped. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_VentBypassTemp.CurrentValue | 2 | r_PAR_VentBypassTemp.CurrentValue | Process temperature above which the vent cycles will be skipped. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_VentBypassTemp.Implemented | 31 | r_PAR_VentBypassTemp.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_VentBypassTemp.Maximum | 2 | r_PAR_VentBypassTemp.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_VentBypassTemp.Minimum | 2 | r_PAR_VentBypassTemp.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_VentBypassTemp.RemoteWriteAccess | 31 | r_PAR_VentBypassTemp.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_VentBypassTemp.RemoteValue | 2 | r_PAR_VentBypassTemp.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressRecoveryDelay |  | n_PAR_LowPressureRecoveryDelay | Wait time before automatically restarting a paused machine once pressure is restored. In units of milliseconds (ms).
| TRUE | PARAMS_DINT | n_PAR_LowPressRecoveryDelay.CurrentValue | 7 | n_PAR_LowPressureRecoveryDelay.CurrentValue | Wait time before automatically restarting a paused machine once pressure is restored. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressRecoveryDelay.Implemented | 31 | n_PAR_LowPressureRecoveryDelay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_LowPressRecoveryDelay.Maximum | 7 | n_PAR_LowPressureRecoveryDelay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_LowPressRecoveryDelay.Minimum | 7 | n_PAR_LowPressureRecoveryDelay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_LowPressRecoveryDelay.RemoteWriteAccess | 31 | n_PAR_LowPressureRecoveryDelay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_LowPressRecoveryDelay.RemoteValue | 7 | n_PAR_LowPressureRecoveryDelay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressRideThrough |  | n_PAR_LowPressureRideThrough | How long to ignore a low pressure condition before pausing machine operation. In units of milliseconds (ms).
| TRUE | PARAMS_DINT | n_PAR_LowPressRideThrough.CurrentValue | 7 | n_PAR_LowPressureRideThrough.CurrentValue | How long to ignore a low pressure condition before pausing machine operation. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressRideThrough.Implemented | 31 | n_PAR_LowPressureRideThrough.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_LowPressRideThrough.Maximum | 7 | n_PAR_LowPressureRideThrough.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_LowPressRideThrough.Minimum | 7 | n_PAR_LowPressureRideThrough.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_LowPressRideThrough.RemoteWriteAccess | 31 | n_PAR_LowPressureRideThrough.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_LowPressRideThrough.RemoteValue | 7 | n_PAR_LowPressureRideThrough.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressStandbyTO |  | n_PAR_LowPressureStandbyTimeout | Exceeding this timeout, while paused due to low pressure, will abandon efforts for an auto-restart. In units of minutes (min).
| TRUE | PARAMS_DINT | n_PAR_LowPressStandbyTO.CurrentValue | 9 | n_PAR_LowPressureStandbyTimeout.CurrentValue | Exceeding this timeout, while paused due to low pressure, will abandon efforts for an auto-restart. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressStandbyTO.Implemented | 31 | n_PAR_LowPressureStandbyTimeout.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_LowPressStandbyTO.Maximum | 9 | n_PAR_LowPressureStandbyTimeout.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_LowPressStandbyTO.Minimum | 9 | n_PAR_LowPressureStandbyTimeout.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_LowPressStandbyTO.RemoteWriteAccess | 31 | n_PAR_LowPressureStandbyTimeout.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_LowPressStandbyTO.RemoteValue | 9 | n_PAR_LowPressureStandbyTimeout.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesPermitted |  | n_PAR_LowPressureStrikesPermitted | Maximum low pressure events permitted which will still result in auto-restart if pressure is restored. In units of events.
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesPermitted.CurrentValue | 28 | n_PAR_LowPressureStrikesPermitted.CurrentValue | Maximum low pressure events permitted which will still result in auto-restart if pressure is restored. This is the current value for this parameter used in operation of the unit. In units of events. | events | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesPermitted.Implemented | 31 | n_PAR_LowPressureStrikesPermitted.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesPermitted.Maximum | 28 | n_PAR_LowPressureStrikesPermitted.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | events
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesPermitted.Minimum | 28 | n_PAR_LowPressureStrikesPermitted.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | events
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesPermitted.RemoteWriteAccess | 31 | n_PAR_LowPressureStrikesPermitted.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesPermitted.RemoteValue | 28 | n_PAR_LowPressureStrikesPermitted.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | events | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesTimer |  | n_PAR_LowPressureStrikesTimer | Rolling time period over which low pressure events are counted to permit/deny an auto-restart. In units of minutes (min).
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesTimer.CurrentValue | 9 | n_PAR_LowPressureStrikesTimer.CurrentValue | Rolling time period over which low pressure events are counted to permit/deny an auto-restart. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesTimer.Implemented | 31 | n_PAR_LowPressureStrikesTimer.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesTimer.Maximum | 9 | n_PAR_LowPressureStrikesTimer.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesTimer.Minimum | 9 | n_PAR_LowPressureStrikesTimer.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesTimer.RemoteWriteAccess | 31 | n_PAR_LowPressureStrikesTimer.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_LowPressStrikesTimer.RemoteValue | 9 | n_PAR_LowPressureStrikesTimer.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSetpoint |  | n_PAR_AdaptiveMaximumSetpoint | Type enumeration: 0=Variable; 1=Fixed 180F; 2: Fixed 190F; 3=Fixed 200F; 4=Fixed 210F; 5=Fixed 220F; 6=Fixed 230F; 7=Fixed 240F; 8=Fixed 250F; 9=Fixed 260F; 10=Fixed 270F; 11=Fixed 280F; 12=Fixed 290F; 13=Fixed 300F
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSetpoint.CurrentValue |  | n_PAR_AdaptiveMaximumSetpoint.CurrentValue | Active enumerated value: 0="Variable"; 1="Fixed 180°F"; 2="Fixed 190°F"; 3="Fixed 200°F"; 4="Fixed 210°F"; 5="Fixed 220°F"; 6="Fixed 230°F"; 7="Fixed 240°F"; 8="Fixed 250°F"; 9="Fixed 260°F"; 10="Fixed 270°F"; 11="Fixed 280°F"; 12="Fixed 290°F"; 13="Fixed 300°F". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSetpoint.Implemented | 31 | n_PAR_AdaptiveMaximumSetpoint.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSetpoint.Maximum |  | n_PAR_AdaptiveMaximumSetpoint.Maximumimum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSetpoint.Minimum |  | n_PAR_AdaptiveMaximumSetpoint.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSetpoint.RemoteWriteAccess | 31 | n_PAR_AdaptiveMaximumSetpoint.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSetpoint.RemoteValue |  | n_PAR_AdaptiveMaximumSetpoint.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_RunLowPressAction |  | n_PAR_RunLowPressureAction | Running Low Pressure Action enumeration: 0=Pause; 1=Warning & lower; 2=Warning & lower with tracking; 3=Just alarm (stop); 4=Alarm (stop) & lower; 5=Max tracking
| TRUE | PARAMS_DINT | n_PAR_RunLowPressAction.CurrentValue |  | n_PAR_RunLowPressureAction.CurrentValue | Selects the reaction to a low pressure condition when the unit is RUNNING. Enumerated value: 0="Pause"; 1="Wrn & Lower SP"; 2="Wrn & Lower SP (Tracking)"; 3="Only Alarm (Stop)"; 4="Alarm (Stop) & Lower SP"; 5="Max SP Tracking". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_RunLowPressAction.Implemented | 31 | n_PAR_RunLowPressureAction.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_RunLowPressAction.Maximum |  | n_PAR_RunLowPressureAction.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_RunLowPressAction.Minimum |  | n_PAR_RunLowPressureAction.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_RunLowPressAction.RemoteWriteAccess | 31 | n_PAR_RunLowPressureAction.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_RunLowPressAction.RemoteValue |  | n_PAR_RunLowPressureAction.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_StopLowPressAction |  | n_PAR_StopLowPressureAction | Stopped Low Pressure Action enumeration: 0=Warning; 1=Warning & lower; 2=Warning & lower with tracking; 3=Alarm; 4=Alarm & lower; 5=Max tracking
| TRUE | PARAMS_DINT | n_PAR_StopLowPressAction.CurrentValue |  | n_PAR_StopLowPressureAction.CurrentValue | Selects the reaction to a low pressure condition when the unit is STOPPED. Enumerated value: 0="Warning"; 1="Warning & Lower SP"; 2="Warning & Lower (Tracking)"; 3="Alarm"; 4="Alarm & Lower SP"; 5="Max Tracking". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_StopLowPressAction.Implemented | 31 | n_PAR_StopLowPressureAction.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_StopLowPressAction.Maximum |  | n_PAR_StopLowPressureAction.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_StopLowPressAction.Minimum |  | n_PAR_StopLowPressureAction.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_StopLowPressAction.RemoteWriteAccess | 31 | n_PAR_StopLowPressureAction.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_StopLowPressAction.RemoteValue |  | n_PAR_StopLowPressureAction.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSP_PressAvg |  | n_PAR_AdaptiveMaximumSetpoint_PressureAverage | How much smoothing to apply to the measured process pressure. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSP_PressAvg.CurrentValue | 8 | n_PAR_AdaptiveMaximumSetpoint_PressureAverage.CurrentValue | How much smoothing to apply to the measured process pressure. This is the current value for this parameter used in operation of the unit. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSP_PressAvg.Implemented | 31 | n_PAR_AdaptiveMaximumSetpoint_PressureAverage.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSP_PressAvg.Maximum | 8 | n_PAR_AdaptiveMaximumSetpoint_PressureAverage.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSP_PressAvg.Minimum | 8 | n_PAR_AdaptiveMaximumSetpoint_PressureAverage.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSP_PressAvg.RemoteWriteAccess | 31 | n_PAR_AdaptiveMaximumSetpoint_PressureAverage.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_AdaptiveMaxSP_PressAvg.RemoteValue | 8 | n_PAR_AdaptiveMaximumSetpoint_PressureAverage.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BootupDuration |  | n_PAR_BootupDuration | Duration between powerup and first scan of the application program. In units of milliseconds (ms).
| TRUE | PARAMS_DINT | n_PAR_BootupDuration.CurrentValue | 7 | n_PAR_BootupDuration.CurrentValue | Duration between powerup and first scan of the application program. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BootupDuration.Implemented | 31 | n_PAR_BootupDuration.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_BootupDuration.Maximum | 7 | n_PAR_BootupDuration.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_BootupDuration.Minimum | 7 | n_PAR_BootupDuration.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_BootupDuration.RemoteWriteAccess | 31 | n_PAR_BootupDuration.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_BootupDuration.RemoteValue | 7 | n_PAR_BootupDuration.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_MoldPurgeTO |  | n_PAR_MoldPurgeTimeout | Maximum duration of a mold purge cycle. Purging will be cancelled if this duration is exceeded. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_MoldPurgeTO.CurrentValue | 8 | n_PAR_MoldPurgeTimeout.CurrentValue | Maximum duration of a mold purge cycle. Purging will be cancelled if this duration is exceeded. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_MoldPurgeTO.Implemented | 31 | n_PAR_MoldPurgeTimeout.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_MoldPurgeTO.Maximum | 8 | n_PAR_MoldPurgeTimeout.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_MoldPurgeTO.Minimum | 8 | n_PAR_MoldPurgeTimeout.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_MoldPurgeTO.RemoteWriteAccess | 31 | n_PAR_MoldPurgeTimeout.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_MoldPurgeTO.RemoteValue | 8 | n_PAR_MoldPurgeTimeout.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_FlowswitchTrip |  | b_PAR_FlowswitchTrip | Trip Type enumeration: FALSE=Trip alarm on contact open; TRUE=Trip alarm on contact closed
| TRUE | PARAMS_BOOL | b_PAR_FlowswitchTrip.CurrentValue |  | b_PAR_FlowswitchTrip.CurrentValue | Selects whether low flow is detected by a flowswitch low or high signal. Enumerated value: FALSE=Trip flow alarm on flowswitch contacts open; TRUE=Trip flow alarm on flowswitch contacts closed. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_FlowswitchTrip.Implemented | 31 | b_PAR_FlowswitchTrip.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_FlowswitchTrip.RemoteWriteAccess | 31 | b_PAR_FlowswitchTrip.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_FlowswitchTrip.RemoteValue | 31 | b_PAR_FlowswitchTrip.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_NetworkHeatCoolEnable |  | b_PAR_NetworkHeatCoolEnable | Network Heat/Cool enumeration: TRUE=Allow heat/cool signals from the network to be acted upon; FALSE=Ignore heat/cool signals from the network.
| TRUE | PARAMS_BOOL | b_PAR_NetworkHeatCoolEnable.CurrentValue |  | b_PAR_NetworkHeatCoolEnable.CurrentValue | Turns on the ability for the unit to receive heat/cool requests from the network connection. Enumerated value: FALSE=Ignore heat/cool signals from the network.; TRUE=Allow heat/cool signals from the network to be acted upon. Not yet implemented. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_NetworkHeatCoolEnable.Implemented | 31 | b_PAR_NetworkHeatCoolEnable.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_NetworkHeatCoolEnable.RemoteWriteAccess | 31 | b_PAR_NetworkHeatCoolEnable.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_NetworkHeatCoolEnable.RemoteValue | 31 | b_PAR_NetworkHeatCoolEnable.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CooldownMaxTime |  | n_PAR_CooldownMaximumTime | If a full cooldown cannot be achieved within this timeframe, the machine will simply stop. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_CooldownMaxTime.CurrentValue | 8 | n_PAR_CooldownMaximumTime.CurrentValue | If a full cooldown cannot be achieved within this timeframe, the machine will simply stop. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CooldownMaxTime.Implemented | 31 | n_PAR_CooldownMaximumTime.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_CooldownMaxTime.Maximum | 8 | n_PAR_CooldownMaximumTime.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_CooldownMaxTime.Minimum | 8 | n_PAR_CooldownMaximumTime.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_CooldownMaxTime.RemoteWriteAccess | 31 | n_PAR_CooldownMaximumTime.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_CooldownMaxTime.RemoteValue | 8 | n_PAR_CooldownMaximumTime.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CooldownMinTime |  | n_PAR_CooldownMinimumTime | If a full cooldown is achieved before this timeframe, the machine will continue to cool until this time. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_CooldownMinTime.CurrentValue | 8 | n_PAR_CooldownMinimumTime.CurrentValue | If a full cooldown is achieved before this timeframe, the machine will continue to cool until this time. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CooldownMinTime.Implemented | 31 | n_PAR_CooldownMinimumTime.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_CooldownMinTime.Maximum | 8 | n_PAR_CooldownMinimumTime.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_CooldownMinTime.Minimum | 8 | n_PAR_CooldownMinimumTime.Minimumimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_CooldownMinTime.RemoteWriteAccess | 31 | n_PAR_CooldownMinimumTime.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_CooldownMinTime.RemoteValue | 8 | n_PAR_CooldownMinimumTime.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_DeviationAction |  | n_PAR_DeviationAction | Deviation Action enumeration: 0=Do Nothing; 1=Warning; 2=Alarm
| TRUE | PARAMS_DINT | n_PAR_DeviationAction.CurrentValue |  | n_PAR_DeviationAction.CurrentValue | Specifies the action that should be taken when a temperature deviation is detected. Enumerated value: 0="Do Nothing"; 1="Warning"; 2="Alarm". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_DeviationAction.Implemented | 31 | n_PAR_DeviationAction.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_DeviationAction.Maximum |  | n_PAR_DeviationAction.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_DeviationAction.Minimum |  | n_PAR_DeviationAction.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_DeviationAction.RemoteWriteAccess | 31 | n_PAR_DeviationAction.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_DeviationAction.RemoteValue |  | n_PAR_DeviationAction.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterK_Factor |  | n_PAR_FlowmeterK_Factor | K-factor of the pulse flowmeter, as determined by the flowmeter's last calibration. In units of pulses per gallon.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterK_Factor.CurrentValue | 18 | n_PAR_FlowmeterK_Factor.CurrentValue | K-factor of the pulse flowmeter, as determined by the flowmeter's last calibration. This is the current value for this parameter used in operation of the unit. In units of pulses/gal. | pulses/gal | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterK_Factor.Implemented | 31 | n_PAR_FlowmeterK_Factor.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_FlowmeterK_Factor.Maximum | 18 | n_PAR_FlowmeterK_Factor.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | pulses/gal
| TRUE | PARAMS_DINT | n_PAR_FlowmeterK_Factor.Minimum | 18 | n_PAR_FlowmeterK_Factor.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | pulses/gal
| TRUE | PARAMS_DINT | n_PAR_FlowmeterK_Factor.RemoteWriteAccess | 31 | n_PAR_FlowmeterK_Factor.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterK_Factor.RemoteValue | 18 | n_PAR_FlowmeterK_Factor.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | pulses/gal | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripAction |  | n_PAR_FlowmeterTripAction | Trip Action enumeration: 0=Do Nothing; 1=Warning; 2=Alarm
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripAction.CurrentValue |  | n_PAR_FlowmeterTripAction.CurrentValue | Specifies the action that should be taken when the flowswitch or flowmeter is tripped. Enumerated value: 0="Do Nothing"; 1="Warning"; 2="Alarm". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripAction.Implemented | 31 | n_PAR_FlowmeterTripAction.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripAction.Maximum |  | n_PAR_FlowmeterTripAction.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripAction.Minimum |  | n_PAR_FlowmeterTripAction.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripAction.RemoteWriteAccess | 31 | n_PAR_FlowmeterTripAction.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripAction.RemoteValue |  | n_PAR_FlowmeterTripAction.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripDelay |  | n_PAR_FlowmeterTripDelay | How long to ignore a low-flow signal from the flow meter before triggering an alarm or warning. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripDelay.CurrentValue | 8 | n_PAR_FlowmeterTripDelay.CurrentValue | How long to ignore a low-flow signal from the flow meter before triggering an alarm or warning. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripDelay.Implemented | 31 | n_PAR_FlowmeterTripDelay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripDelay.Maximum | 8 | n_PAR_FlowmeterTripDelay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripDelay.Minimum | 8 | n_PAR_FlowmeterTripDelay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripDelay.RemoteWriteAccess | 31 | n_PAR_FlowmeterTripDelay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_FlowmeterTripDelay.RemoteValue | 8 | n_PAR_FlowmeterTripDelay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_FlowmeterTripThreshold |  | r_PAR_FlowmeterTripThreshold | Minimum flow required to not produce a low flow warning/alarm. In units of gpm.
| TRUE | PARAMS_REAL | r_PAR_FlowmeterTripThreshold.CurrentValue | 5 | r_PAR_FlowmeterTripThreshold.CurrentValue | Minimum flow required to not produce a low flow warning/alarm. This is the current value for this parameter used in operation of the unit. In units of gpm. | gpm | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_FlowmeterTripThreshold.Implemented | 31 | r_PAR_FlowmeterTripThreshold.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_FlowmeterTripThreshold.Maximum | 5 | r_PAR_FlowmeterTripThreshold.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | gpm
| TRUE | PARAMS_REAL | r_PAR_FlowmeterTripThreshold.Minimum | 5 | r_PAR_FlowmeterTripThreshold.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | gpm
| TRUE | PARAMS_REAL | r_PAR_FlowmeterTripThreshold.RemoteWriteAccess | 31 | r_PAR_FlowmeterTripThreshold.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_FlowmeterTripThreshold.RemoteValue | 5 | r_PAR_FlowmeterTripThreshold.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | gpm | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_HrsWrnThresh |  | n_PAR_HealthCoolingValve_HoursWarningThreshold | Maximum number of cooling valve actuator running hours before the user is prompted to replace it. In units of hours (hr). |  | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_HrsWrnThresh.CurrentValue | 10 | n_PAR_HealthCoolingValve_HoursWarningThreshold.CurrentValue | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_HrsWrnThresh.Implemented | 31 | n_PAR_HealthCoolingValve_HoursWarningThreshold.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_HrsWrnThresh.Maximum | 10 | n_PAR_HealthCoolingValve_HoursWarningThreshold.Maximum | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_HrsWrnThresh.Minimum | 10 | n_PAR_HealthCoolingValve_HoursWarningThreshold.Minimum | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_HrsWrnThresh.RemoteWriteAccess | 31 | n_PAR_HealthCoolingValve_HoursWarningThreshold.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_HrsWrnThresh.RemoteValue | 10 | n_PAR_HealthCoolingValve_HoursWarningThreshold.RemoteValue | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_OpsWrnThresh |  | n_PAR_HealthCoolingValve_OperationsWarningThreshold | Maximum number of cooling valve operations before the user is prompted to replace it. In units of operations. |  | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_OpsWrnThresh.CurrentValue | 17 | n_PAR_HealthCoolingValve_OperationsWarningThreshold.CurrentValue | Not currently implemented. | operations | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_OpsWrnThresh.Implemented | 31 | n_PAR_HealthCoolingValve_OperationsWarningThreshold.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_OpsWrnThresh.Maximum | 17 | n_PAR_HealthCoolingValve_OperationsWarningThreshold.Maximum | Not currently implemented. | operations | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_OpsWrnThresh.Minimum | 17 | n_PAR_HealthCoolingValve_OperationsWarningThreshold.Minimum | Not currently implemented. | operations | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_OpsWrnThresh.RemoteWriteAccess | 31 | n_PAR_HealthCoolingValve_OperationsWarningThreshold.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthCV_OpsWrnThresh.RemoteValue | 17 | n_PAR_HealthCoolingValve_OperationsWarningThreshold.RemoteValue | Not currently implemented. | operations | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthHeaterHrsWrnThresh |  | n_PAR_HealthHeaterHoursWarningThreshold | Maximum number of heater running hours before the user is prompted to replace it. In units of hours (hrs). |  | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthHeaterHrsWrnThresh.CurrentValue | 10 | n_PAR_HealthHeaterHoursWarningThreshold.CurrentValue | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthHeaterHrsWrnThresh.Implemented | 31 | n_PAR_HealthHeaterHoursWarningThreshold.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthHeaterHrsWrnThresh.Maximum | 10 | n_PAR_HealthHeaterHoursWarningThreshold.Maximum | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthHeaterHrsWrnThresh.Minimum | 10 | n_PAR_HealthHeaterHoursWarningThreshold.Minimum | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthHeaterHrsWrnThresh.RemoteWriteAccess | 31 | n_PAR_HealthHeaterHoursWarningThreshold.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthHeaterHrsWrnThresh.RemoteValue | 10 | n_PAR_HealthHeaterHoursWarningThreshold.RemoteValue | Not currently implemented. | hours | Not currently implemented.
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterOpsWrnThresh |  | n_PAR_HealthHeaterOperationsWarningThreshold | Maximum number of heater contactors on/off operations before the user is prompted to replace it. In units of operations (ops).
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterOpsWrnThresh.CurrentValue | 17 | n_PAR_HealthHeaterOperationsWarningThreshold.CurrentValue | Maximum number of heater contactor on/off operations before the user is prompted to replace it. This is the current value for this parameter used in operation of the unit. In units of operations. | operations | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterOpsWrnThresh.Implemented | 31 | n_PAR_HealthHeaterOperationsWarningThreshold.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterOpsWrnThresh.Maximum | 17 | n_PAR_HealthHeaterOperationsWarningThreshold.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | operations
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterOpsWrnThresh.Minimum | 17 | n_PAR_HealthHeaterOperationsWarningThreshold.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | operations
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterOpsWrnThresh.RemoteWriteAccess | 31 | n_PAR_HealthHeaterOperationsWarningThreshold.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterOpsWrnThresh.RemoteValue | 17 | n_PAR_HealthHeaterOperationsWarningThreshold.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | operations | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpHrsWrnThresh |  | n_PAR_HealthPumpHoursWarningThreshold | Maximum number of pump contactor on/off operations before the user is prompted to replace it. In units of hours (hrs). |  | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpHrsWrnThresh.CurrentValue | 10 | n_PAR_HealthPumpHoursWarningThreshold.CurrentValue | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpHrsWrnThresh.Implemented | 31 | n_PAR_HealthPumpHoursWarningThreshold.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpHrsWrnThresh.Maximum | 10 | n_PAR_HealthPumpHoursWarningThreshold.Maximum | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpHrsWrnThresh.Minimum | 10 | n_PAR_HealthPumpHoursWarningThreshold.Minimum | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpHrsWrnThresh.RemoteWriteAccess | 31 | n_PAR_HealthPumpHoursWarningThreshold.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpHrsWrnThresh.RemoteValue | 10 | n_PAR_HealthPumpHoursWarningThreshold.RemoteValue | Not currently implemented. | hours | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpOpsWrnThresh |  | n_PAR_HealthPumpOperationsWarningThreshold | Maximum number of pump running hours before the user is prompted to replace it. In units of operations (ops). |  | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpOpsWrnThresh.CurrentValue | 17 | n_PAR_HealthPumpOperationsWarningThreshold.CurrentValue | Not currently implemented. | operations | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpOpsWrnThresh.Implemented | 31 | n_PAR_HealthPumpOperationsWarningThreshold.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpOpsWrnThresh.Maximum | 17 | n_PAR_HealthPumpOperationsWarningThreshold.Maximum | Not currently implemented. | operations | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpOpsWrnThresh.Minimum | 17 | n_PAR_HealthPumpOperationsWarningThreshold.Minimum | Not currently implemented. | operations | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpOpsWrnThresh.RemoteWriteAccess | 31 | n_PAR_HealthPumpOperationsWarningThreshold.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_DINT | n_PAR_HealthPumpOpsWrnThresh.RemoteValue | 17 | n_PAR_HealthPumpOperationsWarningThreshold.RemoteValue | Not currently implemented. | operations | Not currently implemented.
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterMaxOpsPerHour |  | n_PAR_HealthHeaterMaximumOperationsPerHour | Max heater contactor operations per hour, which will trigger an overuse warning if exceeded. In units of operations per hour (ops/hr).
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterMaxOpsPerHour.CurrentValue | 33 | n_PAR_HealthHeaterMaximumOperationsPerHour.CurrentValue | Max heater contactor operations per hour, which will trigger an overuse warning if exceeded. This is the current value for this parameter used in operation of the unit. In units of operations/hr. | operations/hr | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterMaxOpsPerHour.Implemented | 31 | n_PAR_HealthHeaterMaximumOperationsPerHour.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterMaxOpsPerHour.Maximum | 33 | n_PAR_HealthHeaterMaximumOperationsPerHour.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | operations/hr
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterMaxOpsPerHour.Minimum | 33 | n_PAR_HealthHeaterMaximumOperationsPerHour.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | operations/hr
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterMaxOpsPerHour.RemoteWriteAccess | 31 | n_PAR_HealthHeaterMaximumOperationsPerHour.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HealthHeaterMaxOpsPerHour.RemoteValue | 33 | n_PAR_HealthHeaterMaximumOperationsPerHour.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | operations/hr | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkingBootupDelay |  | n_PAR_NetworkingBootupDelay | Time to wait after bootup before declaring networking errors and/or timeouts. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_NetworkingBootupDelay.CurrentValue | 8 | n_PAR_NetworkingBootupDelay.CurrentValue | Time to wait after bootup before declaring networking errors and/or timeouts. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkingBootupDelay.Implemented | 31 | n_PAR_NetworkingBootupDelay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_NetworkingBootupDelay.Maximum | 8 | n_PAR_NetworkingBootupDelay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_NetworkingBootupDelay.Minimum | 8 | n_PAR_NetworkingBootupDelay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_NetworkingBootupDelay.RemoteWriteAccess | 31 | n_PAR_NetworkingBootupDelay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_NetworkingBootupDelay.RemoteValue | 8 | n_PAR_NetworkingBootupDelay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkModbusStation |  | n_PAR_NetworkModbusStation | Sets the Modbus protocol station ID.
| TRUE | PARAMS_DINT | n_PAR_NetworkModbusStation.CurrentValue |  | n_PAR_NetworkModbusStation.CurrentValue | Sets the Modbus protocol station ID. This is the current value for this parameter used in operation of the unit. | N/A | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkModbusStation.Implemented | 31 | n_PAR_NetworkModbusStation.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_NetworkModbusStation.Maximum |  | n_PAR_NetworkModbusStation.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | N/A
| TRUE | PARAMS_DINT | n_PAR_NetworkModbusStation.Minimum |  | n_PAR_NetworkModbusStation.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | N/A
| TRUE | PARAMS_DINT | n_PAR_NetworkModbusStation.RemoteWriteAccess | 31 | n_PAR_NetworkModbusStation.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_NetworkModbusStation.RemoteValue |  | n_PAR_NetworkModbusStation.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkTO |  | n_PAR_NetworkTimeout | Sets the Modbus protocol timeout. In units of milliseconds (ms).
| TRUE | PARAMS_DINT | n_PAR_NetworkTO.CurrentValue | 7 | n_PAR_NetworkTimeout.CurrentValue | Sets the Modbus protocol timeout. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkTO.Implemented | 31 | n_PAR_NetworkTimeout.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_NetworkTO.Maximum | 7 | n_PAR_NetworkTimeout.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_NetworkTO.Minimum | 7 | n_PAR_NetworkTimeout.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_NetworkTO.RemoteWriteAccess | 31 | n_PAR_NetworkTimeout.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_NetworkTO.RemoteValue | 7 | n_PAR_NetworkTimeout.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkType |  | n_PAR_NetworkType | Network Type enumeration: Bitmask: 00000000=None; xxxxxxx1=Modbus-RTU Slave via RS-485; xxxxxx1x=Modbus-RTU Master via RS-485; xxxxx1xx=Modbus-TCP Slave via Ethernet; xxxx1xxx=Modbus-TCP Master via Ethernet; xxx1xxxx=OPC-UA Client via Ethernet; xx1xxxxx=OPC-UA Server via Ethernet; x1xxxxxx=SPI; 1xxxxxxx=Undefined; Modbus-RTU (master & slave) and SPI will be disabled in first release. .Minimum and .Maximum will be irrelevant since it is a bitmask.
| TRUE | PARAMS_DINT | n_PAR_NetworkType.CurrentValue |  | n_PAR_NetworkType.CurrentValue | Active enumerated value: Bitmask: 00000000="None"; xxxxx1xx="Modbus-TCP Slave via Ethernet"; xxxx1xxx="Modbus-TCP Master via Ethernet"; xxx1xxxx="OPC-UA Client via Ethernet"; xx1xxxxx="OPC-UA Server via Ethernet"; x1xxxxxx="SPI". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkType.Implemented | 31 | n_PAR_NetworkType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_NetworkType.Maximum |  | n_PAR_NetworkType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_NetworkType.Minimum |  | n_PAR_NetworkType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_NetworkType.RemoteWriteAccess | 31 | n_PAR_NetworkType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_NetworkType.RemoteValue |  | n_PAR_NetworkType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeartbeatWarningAlarm |  | n_PAR_HeartbeatWarningAlarm | Lost Network Heatbeat enumeration: 0=None; 1=Warning if disconnected; 2=Warning if absent; 3=Alarm if disconnected; 4=Alarm if absent.
| TRUE | PARAMS_DINT | n_PAR_HeartbeatWarningAlarm.CurrentValue |  | n_PAR_HeartbeatWarningAlarm.CurrentValue | Specifies the action that should be taken when the network heartbeat, once established, is lost. Enumerated value: 0="Nothing"; 1="Warning If Disc"; 2="Warning If Absent"; 3="Alarm If Disc"; 4="Alarm If Absent". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeartbeatWarningAlarm.Implemented | 31 | n_PAR_HeartbeatWarningAlarm.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HeartbeatWarningAlarm.Maximum |  | n_PAR_HeartbeatWarningAlarm.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeartbeatWarningAlarm.Minimum |  | n_PAR_HeartbeatWarningAlarm.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeartbeatWarningAlarm.RemoteWriteAccess | 31 | n_PAR_HeartbeatWarningAlarm.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HeartbeatWarningAlarm.RemoteValue |  | n_PAR_HeartbeatWarningAlarm.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_SetpointSource |  | n_PAR_SetpointSource | Setpoint Source enumeration: 0=Local Main; 1=Local Alternative; 2=Ramp/Soak; 3=Signal; 4=Network; 5=Main/Alt Toggle
| TRUE | PARAMS_DINT | n_PAR_SetpointSource.CurrentValue |  | n_PAR_SetpointSource.CurrentValue | Determine the source of the temperature setpoint for the process loop control. Enumerated value: In parameter list: 0="Main"; 1="Alternative"; 2="Ramp/Soak"; 3="Analog Signal"; 4="Network"; 5="Main/Alt Toggle". On home screen: 0="Main Setpoint"; 1="Alt Setpoint"; 2="Ramp/Soak"; 3="Analog Setpoint"; 4="Network Setpoint" based on n_HD_EffectiveSetpointSource.. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_SetpointSource.Implemented | 31 | n_PAR_SetpointSource.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_SetpointSource.Maximum |  | n_PAR_SetpointSource.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_SetpointSource.Minimum |  | n_PAR_SetpointSource.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_SetpointSource.RemoteWriteAccess | 31 | n_PAR_SetpointSource.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_SetpointSource.RemoteValue |  | n_PAR_SetpointSource.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSource |  | n_PAR_ProcessValueSource | Process Value Source enumeration: 0="To Process RTD"; 1="From Process RTD"; 2="Avg RTD"; 3="Remote RTD"; 4="Analog Signal"; 5="Network".
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSource.CurrentValue |  | n_PAR_ProcessValueSource.CurrentValue | Determines what temperature measurement is used for the loop process value. Enumerated value: 0="To Process RTD"; 1="From Process RTD"; 2="Avg RTD"; 3="Remote RTD"; 4="Analog Signal"; 5="Network". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSource.Implemented | 31 | n_PAR_ProcessValueSource.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSource.Maximum |  | n_PAR_ProcessValueSource.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSource.Minimum |  | n_PAR_ProcessValueSource.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSource.RemoteWriteAccess | 31 | n_PAR_ProcessValueSource.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSource.RemoteValue |  | n_PAR_ProcessValueSource.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSmoothing |  | n_PAR_ProcessValueSmoothing | How much smoothing to apply to the measured process temperature. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSmoothing.CurrentValue | 8 | n_PAR_ProcessValueSmoothing.CurrentValue | How much smoothing to apply to the measured process temperature. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSmoothing.Implemented | 31 | n_PAR_ProcessValueSmoothing.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSmoothing.Maximum | 8 | n_PAR_ProcessValueSmoothing.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSmoothing.Minimum | 8 | n_PAR_ProcessValueSmoothing.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSmoothing.RemoteWriteAccess | 31 | n_PAR_ProcessValueSmoothing.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_ProcessValueSmoothing.RemoteValue | 8 | n_PAR_ProcessValueSmoothing.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_DisplayPV_Smoothing |  | n_PAR_DisplayProcessValue_Smoothing | How much smoothing to apply to the measured process temperature. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_DisplayPV_Smoothing.CurrentValue | 8 | n_PAR_DisplayProcessValue_Smoothing.CurrentValue | How much smoothing to apply to the measured process temperature as displayed on the screen. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_DisplayPV_Smoothing.Implemented | 31 | n_PAR_DisplayProcessValue_Smoothing.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_DisplayPV_Smoothing.Maximum | 8 | n_PAR_DisplayProcessValue_Smoothing.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_DisplayPV_Smoothing.Minimum | 8 | n_PAR_DisplayProcessValue_Smoothing.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_DisplayPV_Smoothing.RemoteWriteAccess | 31 | n_PAR_DisplayProcessValue_Smoothing.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_DisplayPV_Smoothing.RemoteValue | 8 | n_PAR_DisplayProcessValue_Smoothing.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_RampSoakPauseTO |  | n_PAR_RampSoakPauseTimeout | Exceeding this, while paused in Ramp/Soak due to low pressure, will abandon efforts for auto-restart. In units of seconds (s).
| TRUE | PARAMS_DINT | n_PAR_RampSoakPauseTO.CurrentValue | 8 | n_PAR_RampSoakPauseTimeout.CurrentValue | Exceeding this, while paused in Ramp/Soak due to low pressure, will abandon efforts for auto-restart. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_RampSoakPauseTO.Implemented | 31 | n_PAR_RampSoakPauseTimeout.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_RampSoakPauseTO.Maximum | 8 | n_PAR_RampSoakPauseTimeout.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_RampSoakPauseTO.Minimum | 8 | n_PAR_RampSoakPauseTimeout.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_RampSoakPauseTO.RemoteWriteAccess | 31 | n_PAR_RampSoakPauseTimeout.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_RampSoakPauseTO.RemoteValue | 8 | n_PAR_RampSoakPauseTimeout.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_StartupIgnoreDevDelay |  | n_PAR_StartupIgnoreDeviationDelay | How long to ignore temperature deviations after machine startup. In units of minutes (min).
| TRUE | PARAMS_DINT | n_PAR_StartupIgnoreDevDelay.CurrentValue | 9 | n_PAR_StartupIgnoreDeviationDelay.CurrentValue | How long to ignore temperature deviations after machine startup. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_StartupIgnoreDevDelay.Implemented | 31 | n_PAR_StartupIgnoreDeviationDelay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_StartupIgnoreDevDelay.Maximum | 9 | n_PAR_StartupIgnoreDeviationDelay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_StartupIgnoreDevDelay.Minimum | 9 | n_PAR_StartupIgnoreDeviationDelay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_StartupIgnoreDevDelay.RemoteWriteAccess | 31 | n_PAR_StartupIgnoreDeviationDelay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_StartupIgnoreDevDelay.RemoteValue | 9 | n_PAR_StartupIgnoreDeviationDelay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_TempDev_OverSP |  | r_PAR_TempDeviation_OverSetpoint | Process temperature over the setpoint necessary to trigger a high deviation alarm. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_TempDev_OverSP.CurrentValue | 4 | r_PAR_TempDeviation_OverSetpoint.CurrentValue | Process temperature over the setpoint necessary to trigger a high deviation alarm. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_TempDev_OverSP.Implemented | 31 | r_PAR_TempDeviation_OverSetpoint.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_TempDev_OverSP.Maximum | 4 | r_PAR_TempDeviation_OverSetpoint.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_TempDev_OverSP.Minimum | 4 | r_PAR_TempDeviation_OverSetpoint.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_TempDev_OverSP.RemoteWriteAccess | 31 | r_PAR_TempDeviation_OverSetpoint.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_TempDev_OverSP.RemoteValue | 4 | r_PAR_TempDeviation_OverSetpoint.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_TempDev_UnderSP |  | r_PAR_TempDeviation_UnderSetpoint | Process temperature under the setpoint necessary to trigger a low deviation alarm. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_TempDev_UnderSP.CurrentValue | 4 | r_PAR_TempDeviation_UnderSetpoint.CurrentValue | Process temperature under the setpoint necessary to trigger a low deviation alarm. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_TempDev_UnderSP.Implemented | 31 | r_PAR_TempDeviation_UnderSetpoint.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_TempDev_UnderSP.Maximum | 4 | r_PAR_TempDeviation_UnderSetpoint.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_TempDev_UnderSP.Minimum | 4 | r_PAR_TempDeviation_UnderSetpoint.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_TempDev_UnderSP.RemoteWriteAccess | 31 | r_PAR_TempDeviation_UnderSetpoint.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_TempDev_UnderSP.RemoteValue | 4 | r_PAR_TempDeviation_UnderSetpoint.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_TempDev_OverSP_Delay |  | n_PAR_TempDeviation_OverSetpoint_Delay | How long to wait, if a high temperature deviation is detected, before triggering a warning/alarm. In units of minutes (min).
| TRUE | PARAMS_DINT | n_PAR_TempDev_OverSP_Delay.CurrentValue | 9 | n_PAR_TempDeviation_OverSetpoint_Delay.CurrentValue | How long to wait, if a high temperature deviation is detected, before triggering a warning/alarm. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_TempDev_OverSP_Delay.Implemented | 31 | n_PAR_TempDeviation_OverSetpoint_Delay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_TempDev_OverSP_Delay.Maximum | 9 | n_PAR_TempDeviation_OverSetpoint_Delay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_TempDev_OverSP_Delay.Minimum | 9 | n_PAR_TempDeviation_OverSetpoint_Delay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_TempDev_OverSP_Delay.RemoteWriteAccess | 31 | n_PAR_TempDeviation_OverSetpoint_Delay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_TempDev_OverSP_Delay.RemoteValue | 9 | n_PAR_TempDeviation_OverSetpoint_Delay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_TempDev_UnderSP_Delay |  | n_PAR_TempDeviation_UnderSetpoint_Delay | How long to wait, if a low temperature deviation is detected, before triggering a warning/alarm. In units of minutes (min).
| TRUE | PARAMS_DINT | n_PAR_TempDev_UnderSP_Delay.CurrentValue | 9 | n_PAR_TempDeviation_UnderSetpoint_Delay.CurrentValue | How long to wait, if a low temperature deviation is detected, before triggering a warning/alarm. This is the current value for this parameter used in operation of the unit. In units of minutes. | minutes | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_TempDev_UnderSP_Delay.Implemented | 31 | n_PAR_TempDeviation_UnderSetpoint_Delay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_TempDev_UnderSP_Delay.Maximum | 9 | n_PAR_TempDeviation_UnderSetpoint_Delay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_TempDev_UnderSP_Delay.Minimum | 9 | n_PAR_TempDeviation_UnderSetpoint_Delay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | minutes
| TRUE | PARAMS_DINT | n_PAR_TempDev_UnderSP_Delay.RemoteWriteAccess | 31 | n_PAR_TempDeviation_UnderSetpoint_Delay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_TempDev_UnderSP_Delay.RemoteValue | 9 | n_PAR_TempDeviation_UnderSetpoint_Delay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | minutes | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MainTempSetpoint |  | r_PAR_MainTemperatureSetpoint | Main process temperature setpoint for the machine. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_MainTempSetpoint.CurrentValue | 2 | r_PAR_MainTemperatureSetpoint.CurrentValue | Main process temperature setpoint for the machine. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MainTempSetpoint.Implemented | 31 | r_PAR_MainTemperatureSetpoint.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_MainTempSetpoint.Maximum | 2 | r_PAR_MainTemperatureSetpoint.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MainTempSetpoint.Minimum | 2 | r_PAR_MainTemperatureSetpoint.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MainTempSetpoint.RemoteWriteAccess | 31 | r_PAR_MainTemperatureSetpoint.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_MainTempSetpoint.RemoteValue | 2 | r_PAR_MainTemperatureSetpoint.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_AltTempSetpoint |  | r_PAR_AlternateTemperatureSetpoint | Alternative process temperature setpoint for the machine. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_AltTempSetpoint.CurrentValue | 2 | r_PAR_AlternateTemperatureSetpoint.CurrentValue | Alternative process temperature setpoint for the machine. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_AltTempSetpoint.Implemented | 31 | r_PAR_AlternateTemperatureSetpoint.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_AltTempSetpoint.Maximum | 2 | r_PAR_AlternateTemperatureSetpoint.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_AltTempSetpoint.Minimum | 2 | r_PAR_AlternateTemperatureSetpoint.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_AltTempSetpoint.RemoteWriteAccess | 31 | r_PAR_AlternateTemperatureSetpoint.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_AltTempSetpoint.RemoteValue | 2 | r_PAR_AlternateTemperatureSetpoint.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CooldownShutdownTemp |  | r_PAR_CooldownShutdownTemp | Temperature at which Auto Cool Stop is considered complete and the machine will shut down. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_CooldownShutdownTemp.CurrentValue | 2 | r_PAR_CooldownShutdownTemp.CurrentValue | Temperature at which Auto Cool Stop is considered complete and the machine will shut down. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CooldownShutdownTemp.Implemented | 31 | r_PAR_CooldownShutdownTemp.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CooldownShutdownTemp.Maximum | 2 | r_PAR_CooldownShutdownTemp.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_CooldownShutdownTemp.Minimum | 2 | r_PAR_CooldownShutdownTemp.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_CooldownShutdownTemp.RemoteWriteAccess | 31 | r_PAR_CooldownShutdownTemp.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CooldownShutdownTemp.RemoteValue | 2 | r_PAR_CooldownShutdownTemp.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CoolingCycleTime |  | r_PAR_CoolingCycleTime | The cooling valve cycle time, providing the PWM timebase for the cooling valve. In units of seconds.
| TRUE | PARAMS_REAL | r_PAR_CoolingCycleTime.CurrentValue | 8 | r_PAR_CoolingCycleTime.CurrentValue | The cooling valve cycle time, providing the PWM timebase for the cooling valve. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CoolingCycleTime.Implemented | 31 | r_PAR_CoolingCycleTime.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CoolingCycleTime.Maximum | 8 | r_PAR_CoolingCycleTime.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_CoolingCycleTime.Minimum | 8 | r_PAR_CoolingCycleTime.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_CoolingCycleTime.RemoteWriteAccess | 31 | r_PAR_CoolingCycleTime.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CoolingCycleTime.RemoteValue | 8 | r_PAR_CoolingCycleTime.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CoolingMaxPWM |  | r_PAR_CoolingMaximumPWM | Maximum "on time" for the cooling valve. Requests above this will result in 100% cooling. In units of %.
| TRUE | PARAMS_REAL | r_PAR_CoolingMaxPWM.CurrentValue | 11 | r_PAR_CoolingMaximumPWM.CurrentValue | Maximum "on time" for the cooling valve. Requests above this will result in 100% cooling. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CoolingMaxPWM.Implemented | 31 | r_PAR_CoolingMaximumPWM.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CoolingMaxPWM.Maximum | 11 | r_PAR_CoolingMaximumPWM.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CoolingMaxPWM.Minimum | 11 | r_PAR_CoolingMaximumPWM.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CoolingMaxPWM.RemoteWriteAccess | 31 | r_PAR_CoolingMaximumPWM.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CoolingMaxPWM.RemoteValue | 11 | r_PAR_CoolingMaximumPWM.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CoolingMinPWM |  | r_PAR_CoolingMinimumPWM | Minimum "on time" for the cooling valve. Requests below this will result in 0% cooling. In units of %.
| TRUE | PARAMS_REAL | r_PAR_CoolingMinPWM.CurrentValue | 11 | r_PAR_CoolingMinimumPWM.CurrentValue | Minimum "on time" for the cooling valve. Requests below this will result in 0% cooling. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_CoolingMinPWM.Implemented | 31 | r_PAR_CoolingMinimumPWM.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_CoolingMinPWM.Maximum | 11 | r_PAR_CoolingMinimumPWM.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CoolingMinPWM.Minimum | 11 | r_PAR_CoolingMinimumPWM.Minimumimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_CoolingMinPWM.RemoteWriteAccess | 31 | r_PAR_CoolingMinimumPWM.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_CoolingMinPWM.RemoteValue | 11 | r_PAR_CoolingMinimumPWM.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeatingCycleTime |  | r_PAR_HeatingCycleTime | The heater cycle time, providing the PWM timebase for the heater. In units of seconds.
| TRUE | PARAMS_REAL | r_PAR_HeatingCycleTime.CurrentValue | 8 | r_PAR_HeatingCycleTime.CurrentValue | The heater cycle time, providing the PWM timebase for the heater. This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeatingCycleTime.Implemented | 31 | r_PAR_HeatingCycleTime.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_HeatingCycleTime.Maximum | 8 | r_PAR_HeatingCycleTime.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_HeatingCycleTime.Minimum | 8 | r_PAR_HeatingCycleTime.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_HeatingCycleTime.RemoteWriteAccess | 31 | r_PAR_HeatingCycleTime.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_HeatingCycleTime.RemoteValue | 8 | r_PAR_HeatingCycleTime.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeatingMaxPWM |  | r_PAR_HeatingMaximumPWM | Maximum "on time" for the heater. Requests above this will result in 100% heating. In units of %.
| TRUE | PARAMS_REAL | r_PAR_HeatingMaxPWM.CurrentValue | 11 | r_PAR_HeatingMaximumPWM.CurrentValue | Maximum "on time" for the heater. Requests above this will result in 100% heating. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeatingMaxPWM.Implemented | 31 | r_PAR_HeatingMaximumPWM.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_HeatingMaxPWM.Maximum | 11 | r_PAR_HeatingMaximumPWM.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_HeatingMaxPWM.Minimum | 11 | r_PAR_HeatingMaximumPWM.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_HeatingMaxPWM.RemoteWriteAccess | 31 | r_PAR_HeatingMaximumPWM.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_HeatingMaxPWM.RemoteValue | 11 | r_PAR_HeatingMaximumPWM.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeatingMinPWM |  | r_PAR_HeatingMinimumPWM | Minimum "on time" for the heater. Requests below this will result in 0% heating. In units of %.
| TRUE | PARAMS_REAL | r_PAR_HeatingMinPWM.CurrentValue | 11 | r_PAR_HeatingMinimumPWM.CurrentValue | Minimum "on time" for the heater. Requests below this will result in 0% heating. This is the current value for this parameter used in operation of the unit. In units of %. | % | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeatingMinPWM.Implemented | 31 | r_PAR_HeatingMinimumPWM.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_HeatingMinPWM.Maximum | 11 | r_PAR_HeatingMinimumPWM.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_HeatingMinPWM.Minimum | 11 | r_PAR_HeatingMinimumPWM.Minimumimum | The minimum permitted value of .CurrentValue or .RemoteValue. | %
| TRUE | PARAMS_REAL | r_PAR_HeatingMinPWM.RemoteWriteAccess | 31 | r_PAR_HeatingMinimumPWM.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_HeatingMinPWM.RemoteValue | 11 | r_PAR_HeatingMinimumPWM.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | % | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeaterDeadband |  | r_PAR_HeaterDeadband | Magnitude of dynamic heating deadband. (Will be active only when overall cooling is occurring.) In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_HeaterDeadband.CurrentValue | 4 | r_PAR_HeaterDeadband.CurrentValue | Magnitude of dynamic heating deadband. (Will be active only when overall cooling is occurring.) This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HeaterDeadband.Implemented | 31 | r_PAR_HeaterDeadband.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_HeaterDeadband.Maximum | 4 | r_PAR_HeaterDeadband.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_HeaterDeadband.Minimum | 4 | r_PAR_HeaterDeadband.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_HeaterDeadband.RemoteWriteAccess | 31 | r_PAR_HeaterDeadband.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_HeaterDeadband.RemoteValue | 4 | r_PAR_HeaterDeadband.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_DINT | n_PAR_AlgorithmType |  | n_PAR_AlgorithmType | Algorithm Type enumeration:
| FALSE | PARAMS_DINT | n_PAR_AlgorithmType.CurrentValue |  | n_PAR_AlgorithmType.CurrentValue | <enumeration> This is the current value for this parameter used in operation of the unit. | --- | Parameter .Value is only valid if .Implemented is TRUE.
| FALSE | PARAMS_DINT | n_PAR_AlgorithmType.Implemented | 31 | n_PAR_AlgorithmType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| FALSE | PARAMS_DINT | n_PAR_AlgorithmType.Maximum |  | n_PAR_AlgorithmType.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | ---
| FALSE | PARAMS_DINT | n_PAR_AlgorithmType.Minimum |  | n_PAR_AlgorithmType.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | ---
| FALSE | PARAMS_DINT | n_PAR_AlgorithmType.RemoteWriteAccess | 31 | n_PAR_AlgorithmType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| FALSE | PARAMS_DINT | n_PAR_AlgorithmType.RemoteValue |  | n_PAR_AlgorithmType.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | --- | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_P_Band |  | r_PAR_PID_ProportionalBand | Temp band over which P-response will be 100%. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_PID_P_Band.CurrentValue | 4 | r_PAR_PID_ProportionalBand.CurrentValue | Temp band over which P-response will be 100%. Smaller value = more aggressive P-response. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_P_Band.Implemented | 31 | r_PAR_PID_ProportionalBand.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PID_P_Band.Maximum | 4 | r_PAR_PID_ProportionalBand.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_PID_P_Band.Minimum | 4 | r_PAR_PID_ProportionalBand.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_PID_P_Band.RemoteWriteAccess | 31 | r_PAR_PID_ProportionalBand.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PID_P_Band.RemoteValue | 4 | r_PAR_PID_ProportionalBand.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_I_Gain |  | r_PAR_PID_IntegralGain | Temperature PID integral gain. Smaller value = more aggressive I-response, disabled with "0". In units of seconds.
| TRUE | PARAMS_REAL | r_PAR_PID_I_Gain.CurrentValue | 8 | r_PAR_PID_IntegralGain.CurrentValue | Temperature PID integral gain. Smaller value = more aggressive I-response, disabled with "0". This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_I_Gain.Implemented | 31 | r_PAR_PID_IntegralGain.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PID_I_Gain.Maximum | 8 | r_PAR_PID_IntegralGain.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_PID_I_Gain.Minimum | 8 | r_PAR_PID_IntegralGain.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_PID_I_Gain.RemoteWriteAccess | 31 | r_PAR_PID_IntegralGain.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PID_I_Gain.RemoteValue | 8 | r_PAR_PID_IntegralGain.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_D_Gain |  | r_PAR_PID_DerivativeGain | Temperature PID derivative gain. Larger value = more aggressive D-response, disabled with "0". In units of seconds.
| TRUE | PARAMS_REAL | r_PAR_PID_D_Gain.CurrentValue | 8 | r_PAR_PID_DerivativeGain.CurrentValue | Temperature PID derivative gain. Larger value = more aggressive D-response, disabled with "0". This is the current value for this parameter used in operation of the unit. In units of seconds. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_D_Gain.Implemented | 31 | r_PAR_PID_DerivativeGain.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PID_D_Gain.Maximum | 8 | r_PAR_PID_DerivativeGain.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_PID_D_Gain.Minimum | 8 | r_PAR_PID_DerivativeGain.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_REAL | r_PAR_PID_D_Gain.RemoteWriteAccess | 31 | r_PAR_PID_DerivativeGain.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PID_D_Gain.RemoteValue | 8 | r_PAR_PID_DerivativeGain.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_Deadband |  | r_PAR_PID_Deadband | Output deadband for the PID function. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_PID_Deadband.CurrentValue | 4 | r_PAR_PID_Deadband.CurrentValue | Output deadband for the PID function. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_Deadband.Implemented | 31 | r_PAR_PID_Deadband.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PID_Deadband.Maximum | 4 | r_PAR_PID_Deadband.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_PID_Deadband.Minimum | 4 | r_PAR_PID_Deadband.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_PID_Deadband.RemoteWriteAccess | 31 | r_PAR_PID_Deadband.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PID_Deadband.RemoteValue | 4 | r_PAR_PID_Deadband.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_IntegralActiveBand |  | r_PAR_PID_IntegralActiveBand | Temperature band over which the PID integral response is active. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_PID_IntegralActiveBand.CurrentValue | 4 | r_PAR_PID_IntegralActiveBand.CurrentValue | Temperature band over which the PID integral response is active. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_IntegralActiveBand.Implemented | 31 | r_PAR_PID_IntegralActiveBand.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PID_IntegralActiveBand.Maximum | 4 | r_PAR_PID_IntegralActiveBand.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_PID_IntegralActiveBand.Minimum | 4 | r_PAR_PID_IntegralActiveBand.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_PID_IntegralActiveBand.RemoteWriteAccess | 31 | r_PAR_PID_IntegralActiveBand.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PID_IntegralActiveBand.RemoteValue | 4 | r_PAR_PID_IntegralActiveBand.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_DynamicHeatRatioMult |  | r_PAR_PID_DynamicHeatRatioMultiplier | Characterizes the thermal power of cooling vs heating when operating at high process temperatures.
| TRUE | PARAMS_REAL | r_PAR_PID_DynamicHeatRatioMult.CurrentValue |  | r_PAR_PID_DynamicHeatRatioMultiplier.CurrentValue | Characterizes the thermal power of cooling vs heating when operating at high process temperatures. This is the current value for this parameter used in operation of the unit. | --- | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_DynamicHeatRatioMult.Implemented | 31 | r_PAR_PID_DynamicHeatRatioMultiplier.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PID_DynamicHeatRatioMult.Maximum |  | r_PAR_PID_DynamicHeatRatioMultiplier.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | ---
| TRUE | PARAMS_REAL | r_PAR_PID_DynamicHeatRatioMult.Minimum |  | r_PAR_PID_DynamicHeatRatioMultiplier.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | ---
| TRUE | PARAMS_REAL | r_PAR_PID_DynamicHeatRatioMult.RemoteWriteAccess | 31 | r_PAR_PID_DynamicHeatRatioMultiplier.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PID_DynamicHeatRatioMult.RemoteValue |  | r_PAR_PID_DynamicHeatRatioMultiplier.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | --- | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_HeatToCoolOutRatio |  | r_PAR_PID_HeatToCoolOutputRatio | Value of 1.0=equal heating/cooling. Values <1.0 for large heaters. Values >1.0 for small heaters.
| TRUE | PARAMS_REAL | r_PAR_PID_HeatToCoolOutRatio.CurrentValue |  | r_PAR_PID_HeatToCoolOutputRatio.CurrentValue | Value of 1.0=equal heating/cooling. Values <1.0 for large heaters. Values >1.0 for small heaters. This is the current value for this parameter used in operation of the unit. | --- | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PID_HeatToCoolOutRatio.Implemented | 31 | r_PAR_PID_HeatToCoolOutputRatio.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PID_HeatToCoolOutRatio.Maximum |  | r_PAR_PID_HeatToCoolOutputRatio.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | ---
| TRUE | PARAMS_REAL | r_PAR_PID_HeatToCoolOutRatio.Minimum |  | r_PAR_PID_HeatToCoolOutputRatio.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | ---
| TRUE | PARAMS_REAL | r_PAR_PID_HeatToCoolOutRatio.RemoteWriteAccess | 31 | r_PAR_PID_HeatToCoolOutputRatio.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PID_HeatToCoolOutRatio.RemoteValue |  | r_PAR_PID_HeatToCoolOutputRatio.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | --- | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_ProcessDB_Threshold |  | r_PAR_ProcessDeadband_Threshold | Magnitude of accumulated process cooling that is required to enable heating deadbanding. In units of Δ°C·sec.
| TRUE | PARAMS_REAL | r_PAR_ProcessDB_Threshold.CurrentValue | 34 | r_PAR_ProcessDeadband_Threshold.CurrentValue | Magnitude of accumulated process cooling that is required to enable heating deadbanding. This is the current value for this parameter used in operation of the unit. In units of Δ°C·sec. | Δ°C·sec | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_ProcessDB_Threshold.Implemented | 31 | r_PAR_ProcessDeadband_Threshold.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_ProcessDB_Threshold.Maximum | 34 | r_PAR_ProcessDeadband_Threshold.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C·sec
| TRUE | PARAMS_REAL | r_PAR_ProcessDB_Threshold.Minimum | 34 | r_PAR_ProcessDeadband_Threshold.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C·sec
| TRUE | PARAMS_REAL | r_PAR_ProcessDB_Threshold.RemoteWriteAccess | 31 | r_PAR_ProcessDeadband_Threshold.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_ProcessDB_Threshold.RemoteValue | 34 | r_PAR_ProcessDeadband_Threshold.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C·sec | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_SupplyRTD_CalOffset |  | r_PAR_SupplyRTD_CalibrationOffset | Defines a calibration offset for the "To Process" RTD temperature sensor. in units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_SupplyRTD_CalOffset.CurrentValue | 4 | r_PAR_SupplyRTD_CalibrationOffset.CurrentValue | Defines a calibration offset for the "To Process" RTD temperature sensor. This is the current value for this parameter used in operation of the unit. in units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_SupplyRTD_CalOffset.Implemented | 31 | r_PAR_SupplyRTD_CalibrationOffset.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_SupplyRTD_CalOffset.Maximum | 4 | r_PAR_SupplyRTD_CalibrationOffset.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_SupplyRTD_CalOffset.Minimum | 4 | r_PAR_SupplyRTD_CalibrationOffset.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_SupplyRTD_CalOffset.RemoteWriteAccess | 31 | r_PAR_SupplyRTD_CalibrationOffset.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_SupplyRTD_CalOffset.RemoteValue | 4 | r_PAR_SupplyRTD_CalibrationOffset.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_ReturnRTD_CalOffset |  | r_PAR_ReturnRTD_CalibrationOffset | Defines a calibration offset for the "From Process" RTD temperature sensor. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_ReturnRTD_CalOffset.CurrentValue | 4 | r_PAR_ReturnRTD_CalibrationOffset.CurrentValue | Defines a calibration offset for the "From Process" RTD temperature sensor. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_ReturnRTD_CalOffset.Implemented | 31 | r_PAR_ReturnRTD_CalibrationOffset.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_ReturnRTD_CalOffset.Maximum | 4 | r_PAR_ReturnRTD_CalibrationOffset.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_ReturnRTD_CalOffset.Minimum | 4 | r_PAR_ReturnRTD_CalibrationOffset.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_ReturnRTD_CalOffset.RemoteWriteAccess | 31 | r_PAR_ReturnRTD_CalibrationOffset.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_ReturnRTD_CalOffset.RemoteValue | 4 | r_PAR_ReturnRTD_CalibrationOffset.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_RemoteRTD_CalOffset |  | r_PAR_RemoteRTD_CalibrationOffset | Defines a calibration offset for the Remote RTD temperature sensor. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_RemoteRTD_CalOffset.CurrentValue | 4 | r_PAR_RemoteRTD_CalibrationOffset.CurrentValue | Defines a calibration offset for the Remote RTD temperature sensor. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_RemoteRTD_CalOffset.Implemented | 31 | r_PAR_RemoteRTD_CalibrationOffset.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_RemoteRTD_CalOffset.Maximum | 4 | r_PAR_RemoteRTD_CalibrationOffset.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_RemoteRTD_CalOffset.Minimum | 4 | r_PAR_RemoteRTD_CalibrationOffset.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_RemoteRTD_CalOffset.RemoteWriteAccess | 31 | r_PAR_RemoteRTD_CalibrationOffset.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_RemoteRTD_CalOffset.RemoteValue | 4 | r_PAR_RemoteRTD_CalibrationOffset.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_REAL | r_PAR_NetworkProcessCalOffset |  | r_PAR_NetworkProcessCalibrationOffset | Defines a calibration offset for process temperature value received over the network.
| FALSE | PARAMS_REAL | r_PAR_NetworkProcessCalOffset.CurrentValue | 4 | r_PAR_NetworkProcessCalibrationOffset.CurrentValue | Not currently implemented. | Δ°C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_NetworkProcessCalOffset.Implemented | 31 | r_PAR_NetworkProcessCalibrationOffset.Implemented | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_NetworkProcessCalOffset.Maximum | 4 | r_PAR_NetworkProcessCalibrationOffset.Maximum | Not currently implemented. | Δ°C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_NetworkProcessCalOffset.Minimum | 4 | r_PAR_NetworkProcessCalibrationOffset.Minimum | Not currently implemented. | Δ°C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_NetworkProcessCalOffset.RemoteWriteAccess | 31 | r_PAR_NetworkProcessCalibrationOffset.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_NetworkProcessCalOffset.RemoteValue | 4 | r_PAR_NetworkProcessCalibrationOffset.RemoteValue | Not currently implemented. | Δ°C | Not currently implemented.
| TRUE | PARAMS_REAL | r_PAR_TwoWireRTD_Offset |  | r_PAR_TwoWireRTD_Offset | Defines a calibration offset on 2-wire RTD temperature sensors to compensate for lead resistance. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_TwoWireRTD_Offset.CurrentValue | 4 | r_PAR_TwoWireRTD_Offset.CurrentValue | Defines a calibration offset on 2-wire RTD temperature sensors to compensate for lead resistance. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_TwoWireRTD_Offset.Implemented | 31 | r_PAR_TwoWireRTD_Offset.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_TwoWireRTD_Offset.Maximum | 4 | r_PAR_TwoWireRTD_Offset.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_TwoWireRTD_Offset.Minimum | 4 | r_PAR_TwoWireRTD_Offset.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_TwoWireRTD_Offset.RemoteWriteAccess | 31 | r_PAR_TwoWireRTD_Offset.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_TwoWireRTD_Offset.RemoteValue | 4 | r_PAR_TwoWireRTD_Offset.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_UserTempHighAlarm |  | r_PAR_UserTemperatureHighAlarm | Temperature above which an operator-defined high-temperature alarm will occur. In units of degrees Celsius.
| TRUE | PARAMS_REAL | r_PAR_UserTempHighAlarm.CurrentValue | 2 | r_PAR_UserTemperatureHighAlarm.CurrentValue | Temperature above which an operator-defined high-temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_UserTempHighAlarm.Implemented | 31 | r_PAR_UserTemperatureHighAlarm.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_UserTempHighAlarm.Maximum | 2 | r_PAR_UserTemperatureHighAlarm.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_UserTempHighAlarm.Minimum | 2 | r_PAR_UserTemperatureHighAlarm.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_UserTempHighAlarm.RemoteWriteAccess | 31 | r_PAR_UserTemperatureHighAlarm.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_UserTempHighAlarm.RemoteValue | 2 | r_PAR_UserTemperatureHighAlarm.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_UserTempLowAlarm |  | r_PAR_UserTemperatureLowAlarm | Temperature under which an operator-defined low-temperature alarm will occur. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_UserTempLowAlarm.CurrentValue | 2 | r_PAR_UserTemperatureLowAlarm.CurrentValue | Temperature under which an operator-defined low-temperature alarm will occur. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_UserTempLowAlarm.Implemented | 31 | r_PAR_UserTemperatureLowAlarm.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_UserTempLowAlarm.Maximum | 2 | r_PAR_UserTemperatureLowAlarm.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_UserTempLowAlarm.Minimum | 2 | r_PAR_UserTemperatureLowAlarm.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_UserTempLowAlarm.RemoteWriteAccess | 31 | r_PAR_UserTemperatureLowAlarm.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_UserTempLowAlarm.RemoteValue | 2 | r_PAR_UserTemperatureLowAlarm.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FluidType |  | n_PAR_FluidType | Fluid Type enumeration: 0=Water; 1=25% Ethylene Glycol/75% Water; 2=50% Ethylene Glycol/75% Water
| TRUE | PARAMS_DINT | n_PAR_FluidType.CurrentValue |  | n_PAR_FluidType.CurrentValue | Selects whether the process is using pure water or a water/glycol mix. Enumerated value: 0=Water; 1=25% Ethylene Glycol/75% Water; 2=50% Ethylene Glycol/75% Water. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_FluidType.Implemented | 31 | n_PAR_FluidType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_FluidType.Maximum |  | n_PAR_FluidType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_FluidType.Minimum |  | n_PAR_FluidType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_FluidType.RemoteWriteAccess | 31 | n_PAR_FluidType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_FluidType.RemoteValue |  | n_PAR_FluidType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PlumbingCv |  | r_PAR_PlumbingCv | Cv of the connected facility plumbing. Anything greater than 100 is considered negligible. In units of gal/min/psi.
| TRUE | PARAMS_REAL | r_PAR_PlumbingCv.CurrentValue | 12 | r_PAR_PlumbingCv.CurrentValue | Cv of the connected facility plumbing. Anything greater than 100 is considered negligible. This is the current value for this parameter used in operation of the unit. In units of gal/min/psi. | gal/min/psi | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_PlumbingCv.Implemented | 31 | r_PAR_PlumbingCv.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_PlumbingCv.Maximum | 12 | r_PAR_PlumbingCv.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | gal/min/psi
| TRUE | PARAMS_REAL | r_PAR_PlumbingCv.Minimum | 12 | r_PAR_PlumbingCv.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | gal/min/psi
| TRUE | PARAMS_REAL | r_PAR_PlumbingCv.RemoteWriteAccess | 31 | r_PAR_PlumbingCv.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_PlumbingCv.RemoteValue | 12 | r_PAR_PlumbingCv.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | gal/min/psi | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_Language |  | n_PAR_Language | Language enumeration: 0=English
| TRUE | PARAMS_DINT | n_PAR_Language.CurrentValue |  | n_PAR_Language.CurrentValue | Language selection for touchscreen. Enumerated value: 0="English". | <enumeration> | Currently only 1 setting (English)
| TRUE | PARAMS_DINT | n_PAR_Language.Implemented | 31 | n_PAR_Language.Implemented | Currently only 1 setting (English) | Yes/No | Currently only 1 setting (English)
| TRUE | PARAMS_DINT | n_PAR_Language.Maximum |  | n_PAR_Language.Maximum | Currently only 1 setting (English) | <enumeration> | Currently only 1 setting (English)
| TRUE | PARAMS_DINT | n_PAR_Language.Minimum |  | n_PAR_Language.Minimum | Currently only 1 setting (English) | <enumeration> | Currently only 1 setting (English)
| TRUE | PARAMS_DINT | n_PAR_Language.RemoteWriteAccess | 31 | n_PAR_Language.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Currently only 1 setting (English)
| TRUE | PARAMS_DINT | n_PAR_Language.RemoteValue |  | n_PAR_Language.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | Currently only 1 setting (English)
| TRUE | PARAMS_REAL | r_PAR_MaxPanelTemp |  | r_PAR_MaximumPanelTemp | Temperature above which an electrical panel high temperature alarm will be triggered. In units of °C.
| TRUE | PARAMS_REAL | r_PAR_MaxPanelTemp.CurrentValue | 2 | r_PAR_MaximumPanelTemp.CurrentValue | Temperature above which an electrical panel high temperature alarm will be triggered. This is the current value for this parameter used in operation of the unit. In units of °C. | °C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MaxPanelTemp.Implemented | 31 | r_PAR_MaximumPanelTemp.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_MaxPanelTemp.Maximum | 2 | r_PAR_MaximumPanelTemp.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MaxPanelTemp.Minimum | 2 | r_PAR_MaximumPanelTemp.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | °C
| TRUE | PARAMS_REAL | r_PAR_MaxPanelTemp.RemoteWriteAccess | 31 | r_PAR_MaximumPanelTemp.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_MaxPanelTemp.RemoteValue | 2 | r_PAR_MaximumPanelTemp.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | °C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_EnclosureTempOffset |  | r_PAR_EnclosureTemperatureOffset | Difference between temperature sensor and the actual electrical enclosure ambient temperature. In units of Δ°C.
| TRUE | PARAMS_REAL | r_PAR_EnclosureTempOffset.CurrentValue | 4 | r_PAR_EnclosureTemperatureOffset.CurrentValue | Difference between temperature sensor and the actual electrical enclosure ambient temperature. This is the current value for this parameter used in operation of the unit. In units of Δ°C. | Δ°C | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_EnclosureTempOffset.Implemented | 31 | r_PAR_EnclosureTemperatureOffset.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_EnclosureTempOffset.Maximum | 4 | r_PAR_EnclosureTemperatureOffset.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_EnclosureTempOffset.Minimum | 4 | r_PAR_EnclosureTemperatureOffset.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δ°C
| TRUE | PARAMS_REAL | r_PAR_EnclosureTempOffset.RemoteWriteAccess | 31 | r_PAR_EnclosureTemperatureOffset.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_EnclosureTempOffset.RemoteValue | 4 | r_PAR_EnclosureTemperatureOffset.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δ°C | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MaxPressure |  | r_PAR_MaximumPressure | From-process pressure above this value will trigger a high-pressure alarm. In units of psi.
| TRUE | PARAMS_REAL | r_PAR_MaxPressure.CurrentValue | 13 | r_PAR_MaximumPressure.CurrentValue | From-process pressure above this value will trigger a high-pressure alarm. This is the current value for this parameter used in operation of the unit. In units of psi. | psi | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_MaxPressure.Implemented | 31 | r_PAR_MaximumPressure.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_MaxPressure.Maximum | 13 | r_PAR_MaximumPressure.Maximumimum | The maximum permitted value of .CurrentValue or .RemoteValue. | psi
| TRUE | PARAMS_REAL | r_PAR_MaxPressure.Minimum | 13 | r_PAR_MaximumPressure.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | psi
| TRUE | PARAMS_REAL | r_PAR_MaxPressure.RemoteWriteAccess | 31 | r_PAR_MaximumPressure.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_MaxPressure.RemoteValue | 13 | r_PAR_MaximumPressure.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | psi | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_AutoHotPressureReliefPress |  | r_PAR_AutoHotPressureReliefPressure | Pressure at which the automatic hot pressure relief will be triggered.
| TRUE | PARAMS_REAL | r_PAR_AutoHotPressureReliefPress.CurrentValue | 13 | r_PAR_AutoHotPressureReliefPressure.CurrentValue | Pressure at which the automatic hot pressure relief will be triggered. This is the current value for this parameter used in operation of the unit. In units of pounds per square inch (psi). | psi | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_AutoHotPressureReliefPress.Implemented | 31 | r_PAR_AutoHotPressureReliefPressure.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_AutoHotPressureReliefPress.Maximum | 13 | r_PAR_AutoHotPressureReliefPressure.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | psi
| TRUE | PARAMS_REAL | r_PAR_AutoHotPressureReliefPress.Minimum | 13 | r_PAR_AutoHotPressureReliefPressure.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | psi
| TRUE | PARAMS_REAL | r_PAR_AutoHotPressureReliefPress.RemoteWriteAccess | 31 | r_PAR_AutoHotPressureReliefPressure.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_AutoHotPressureReliefPress.RemoteValue | 13 | r_PAR_AutoHotPressureReliefPressure.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | psi | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_SoftwareVersion |  | r_PAR_SoftwareVersion | Application software version.
| TRUE | PARAMS_REAL | r_PAR_SoftwareVersion.CurrentValue |  | r_PAR_SoftwareVersion.CurrentValue | Application software version. This is the current value for this parameter used in operation of the unit. | N/A | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_SoftwareVersion.Implemented | 31 | r_PAR_SoftwareVersion.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_SoftwareVersion.Maximum |  | r_PAR_SoftwareVersion.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | N/A
| TRUE | PARAMS_REAL | r_PAR_SoftwareVersion.Minimum |  | r_PAR_SoftwareVersion.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | N/A
| TRUE | PARAMS_REAL | r_PAR_SoftwareVersion.RemoteWriteAccess | 31 | r_PAR_SoftwareVersion.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_SoftwareVersion.RemoteValue |  | r_PAR_SoftwareVersion.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlOutputLimit |  | r_PAR_PID_Autotune_ControlOutputLimit | Autotune: The maximum safe limit that produces the Autotune Process Value Limit. |  | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlOutputLimit.CurrentValue | 11 | r_PAR_PID_Autotune_ControlOutputLimit.CurrentValue | Not currently implemented. | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlOutputLimit.Implemented | 31 | r_PAR_PID_Autotune_ControlOutputLimit.Implemented | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlOutputLimit.Maximum | 11 | r_PAR_PID_Autotune_ControlOutputLimit.Maximum | Not currently implemented | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlOutputLimit.Minimum | 11 | r_PAR_PID_Autotune_ControlOutputLimit.Minimum | Not currently implemented | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlOutputLimit.RemoteWriteAccess | 31 | r_PAR_PID_Autotune_ControlOutputLimit.RemoteWriteAccess | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlOutputLimit.RemoteValue | 11 | r_PAR_PID_Autotune_ControlOutputLimit.RemoteValue | Not currently implemented | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlStepChange |  | r_PAR_PID_Autotune_ControlStepChange | Autotune: Set to 1/3 of 60% of the Autotune Control Output Limit for large cold start steps. |  | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlStepChange.CurrentValue | 11 | r_PAR_PID_Autotune_ControlStepChange.CurrentValue | Not currently implemented | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlStepChange.Implemented | 31 | r_PAR_PID_Autotune_ControlStepChange.Implemented | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlStepChange.Maximum | 11 | r_PAR_PID_Autotune_ControlStepChange.Maximum | Not currently implemented | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlStepChange.Minimum | 11 | r_PAR_PID_Autotune_ControlStepChange.Minimum | Not currently implemented | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlStepChange.RemoteWriteAccess | 31 | r_PAR_PID_Autotune_ControlStepChange.RemoteWriteAccess | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ControlStepChange.RemoteValue | 11 | r_PAR_PID_Autotune_ControlStepChange.RemoteValue | Not currently implemented | % | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_LambdaMultiplier |  | r_PAR_PID_Autotune_LambdaMultiplier | Autotune: Lambda multiplier. Less produces a more aggressive response, typical range 1.5 to 4.0. |  | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_LambdaMultiplier.CurrentValue |  | r_PAR_PID_Autotune_LambdaMultiplier.CurrentValue | Not currently implemented | N/A | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_LambdaMultiplier.Implemented | 31 | r_PAR_PID_Autotune_LambdaMultiplier.Implemented | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_LambdaMultiplier.Maximum |  | r_PAR_PID_Autotune_LambdaMultiplier.Maximum | Not currently implemented | N/A | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_LambdaMultiplier.Minimum |  | r_PAR_PID_Autotune_LambdaMultiplier.Minimum | Not currently implemented | N/A | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_LambdaMultiplier.RemoteWriteAccess | 31 | r_PAR_PID_Autotune_LambdaMultiplier.RemoteWriteAccess | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_LambdaMultiplier.RemoteValue |  | r_PAR_PID_Autotune_LambdaMultiplier.RemoteValue | Not currently implemented | N/A | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_Deadband |  | r_PAR_PID_Autotune_Deadband | Autotune: Process variable dead band. Amount of noise rejection to isolate a clear temperature swing. |  | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_Deadband.CurrentValue | 2 | r_PAR_PID_Autotune_Deadband.CurrentValue | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_Deadband.Implemented | 31 | r_PAR_PID_Autotune_Deadband.Implemented | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_Deadband.Maximum | 2 | r_PAR_PID_Autotune_Deadband.Maximum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_Deadband.Minimum | 2 | r_PAR_PID_Autotune_Deadband.Minimum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_Deadband.RemoteWriteAccess | 31 | r_PAR_PID_Autotune_Deadband.RemoteWriteAccess | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_Deadband.RemoteValue | 2 | r_PAR_PID_Autotune_Deadband.RemoteValue | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MinProcValueAt0 |  | r_PAR_PID_Autotune_MinProcValueAt0 | Autotune: The known minimum process value when Co equals 0%. |  | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MinProcValueAt0.CurrentValue | 2 | r_PAR_PID_Autotune_MinProcValueAt0.CurrentValue | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MinProcValueAt0.Implemented | 31 | r_PAR_PID_Autotune_MinProcValueAt0.Implemented | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MinProcValueAt0.Maximum | 2 | r_PAR_PID_Autotune_MinProcValueAt0.Maximum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MinProcValueAt0.Minimum | 2 | r_PAR_PID_Autotune_MinProcValueAt0.Minimum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MinProcValueAt0.RemoteWriteAccess | 31 | r_PAR_PID_Autotune_MinProcValueAt0.RemoteWriteAccess | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MinProcValueAt0.RemoteValue | 2 | r_PAR_PID_Autotune_MinProcValueAt0.RemoteValue | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MaxProcValueAt100 |  | r_PAR_PID_Autotune_MaxProcValueAt100 | Autotune: The known maximum process value when Co equals 100%. |  | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MaxProcValueAt100.CurrentValue | 2 | r_PAR_PID_Autotune_MaxProcValueAt100.CurrentValue | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MaxProcValueAt100.Implemented | 31 | r_PAR_PID_Autotune_MaxProcValueAt100.Implemented | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MaxProcValueAt100.Maximum | 2 | r_PAR_PID_Autotune_MaxProcValueAt100.Maximum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MaxProcValueAt100.Minimum | 2 | r_PAR_PID_Autotune_MaxProcValueAt100.Minimum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MaxProcValueAt100.RemoteWriteAccess | 31 | r_PAR_PID_Autotune_MaxProcValueAt100.RemoteWriteAccess | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_MaxProcValueAt100.RemoteValue | 2 | r_PAR_PID_Autotune_MaxProcValueAt100.RemoteValue | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ProcessValueLimit |  | r_PAR_PID_Autotune_ProcessValueLimit | Autotune: The maximum limit for the process variable, autotune cycle aborts when exceeded. |  | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ProcessValueLimit.CurrentValue | 2 | r_PAR_PID_Autotune_ProcessValueLimit.CurrentValue | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ProcessValueLimit.Implemented | 31 | r_PAR_PID_Autotune_ProcessValueLimit.Implemented | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ProcessValueLimit.Maximum | 2 | r_PAR_PID_Autotune_ProcessValueLimit.Maximum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ProcessValueLimit.Minimum | 2 | r_PAR_PID_Autotune_ProcessValueLimit.Minimum | Not currently implemented | °C | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ProcessValueLimit.RemoteWriteAccess | 31 | r_PAR_PID_Autotune_ProcessValueLimit.RemoteWriteAccess | Not currently implemented | Yes/No | Not currently implemented.
| FALSE | PARAMS_REAL | r_PAR_PID_AT_ProcessValueLimit.RemoteValue | 2 | r_PAR_PID_Autotune_ProcessValueLimit.RemoteValue | Not currently implemented | °C | Not currently implemented.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefAnticipate |  | r_PAR_HotPressureReliefAnticipate | How far below the hot pressure relief threshold to anticipate the need to automatically relieve. In units of Δpsi.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefAnticipate.CurrentValue | 15 | r_PAR_HotPressureReliefAnticipate.CurrentValue | How far below the hot pressure relief threshold to anticipate the need to automatically relieve. This is the current value for this parameter used in operation of the unit. In units of Δpsi. | Δpsi | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefAnticipate.Implemented | 31 | r_PAR_HotPressureReliefAnticipate.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefAnticipate.Maximum | 15 | r_PAR_HotPressureReliefAnticipate.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefAnticipate.Minimum | 15 | r_PAR_HotPressureReliefAnticipate.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefAnticipate.RemoteWriteAccess | 31 | r_PAR_HotPressureReliefAnticipate.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefAnticipate.RemoteValue | 15 | r_PAR_HotPressureReliefAnticipate.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δpsi | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefHysteresis |  | r_PAR_HotPressureReliefHysteresis | How much pressure drop is required during hot pressure relief to consider the relief complete. In units of Δpsi.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefHysteresis.CurrentValue | 15 | r_PAR_HotPressureReliefHysteresis.CurrentValue | How much pressure drop is required during hot pressure relief to consider the relief complete. This is the current value for this parameter used in operation of the unit. In units of Δpsi. | Δpsi | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefHysteresis.Implemented | 31 | r_PAR_HotPressureReliefHysteresis.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefHysteresis.Maximum | 15 | r_PAR_HotPressureReliefHysteresis.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefHysteresis.Minimum | 15 | r_PAR_HotPressureReliefHysteresis.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | Δpsi
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefHysteresis.RemoteWriteAccess | 31 | r_PAR_HotPressureReliefHysteresis.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_REAL | r_PAR_HotPressReliefHysteresis.RemoteValue | 15 | r_PAR_HotPressureReliefHysteresis.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Δpsi | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkSpi485Baudrate |  | n_PAR_NetworkSpi485Baudrate | SPI baud rate enumeration: 1="2400 bps"; 2="4800 bps"; 3="9600 bps"; 4="19200 bps"; 5="38400 bps"; 7="57600 bps"; 8="115200 bps" (there is no valid speed for "6").
| TRUE | PARAMS_DINT | n_PAR_NetworkSpi485Baudrate.CurrentValue |  | n_PAR_NetworkSpi485Baudrate.CurrentValue | Sets the SPI via RS-485 protocol baud rate. Enumerated value: 1="2400 bps"; 2="4800 bps"; 3="9600 bps"; 4="19200 bps"; 5="38400 bps"; 7="57600 bps"; 8="115200 bps" (there is no valid speed for "6").. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkSpi485Baudrate.Implemented | 31 | n_PAR_NetworkSpi485Baudrate.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_NetworkSpi485Baudrate.Maximum |  | n_PAR_NetworkSpi485Baudrate.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_NetworkSpi485Baudrate.Minimum |  | n_PAR_NetworkSpi485Baudrate.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_NetworkSpi485Baudrate.RemoteWriteAccess | 31 | n_PAR_NetworkSpi485Baudrate.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_NetworkSpi485Baudrate.RemoteValue |  | n_PAR_NetworkSpi485Baudrate.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkSpiStation |  | n_PAR_NetworkSpiStation | Sets the SPI protocol device address. This decimal value is added to the default device address of 20 hex (32 decimal).
| TRUE | PARAMS_DINT | n_PAR_NetworkSpiStation.CurrentValue |  | n_PAR_NetworkSpiStation.CurrentValue | Sets the SPI protocol device address. This decimal value is added to the default device address of 20 hex (32 decimal). This is the current value for this parameter used in operation of the unit. | station number | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_NetworkSpiStation.Implemented | 31 | n_PAR_NetworkSpiStation.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_NetworkSpiStation.Maximum | #N/A | n_PAR_NetworkSpiStation.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | station number
| TRUE | PARAMS_DINT | n_PAR_NetworkSpiStation.Minimum | #N/A | n_PAR_NetworkSpiStation.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | station number
| TRUE | PARAMS_DINT | n_PAR_NetworkSpiStation.RemoteWriteAccess | 31 | n_PAR_NetworkSpiStation.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_NetworkSpiStation.RemoteValue |  | n_PAR_NetworkSpiStation.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | station number | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_EstimatedFlowrateEnable |  | b_PAR_EstimatedFlowrateEnable | Estimated Flowrate enumeration: TRUE=Allow Estimated Flowrate; FALSE=Do Not Allow Estimated Flowrate
| TRUE | PARAMS_BOOL | b_PAR_EstimatedFlowrateEnable.CurrentValue |  | b_PAR_EstimatedFlowrateEnable.CurrentValue | Enables the calculation of estimated flow from the differential pressure across the pump. Enumerated value: FALSE=Estimated flowrate calculation disabled.; TRUE=Estimated flowrate calculation enabled. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_EstimatedFlowrateEnable.Implemented | 31 | b_PAR_EstimatedFlowrateEnable.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_EstimatedFlowrateEnable.RemoteWriteAccess | 31 | b_PAR_EstimatedFlowrateEnable.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_EstimatedFlowrateEnable.RemoteValue | 31 | b_PAR_EstimatedFlowrateEnable.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_DHCP_Enable |  | b_PAR_DHCP_Enable | Auto Restart enumeration: TRUE=Allow Auto Restart; FALSE=Do Not Allow Auto Restart
| TRUE | PARAMS_BOOL | b_PAR_DHCP_Enable.CurrentValue |  | b_PAR_DHCP_Enable.CurrentValue | Enables dynamic IP address assignment. Enumerated value: FALSE=DHCP disabled (static IP addresses); TRUE=DHCP enabled (dynamic IP addresses). | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_DHCP_Enable.Implemented | 31 | b_PAR_DHCP_Enable.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_DHCP_Enable.RemoteWriteAccess | 31 | b_PAR_DHCP_Enable.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_DHCP_Enable.RemoteValue | 31 | b_PAR_DHCP_Enable.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpType |  | n_PAR_PumpType | Pump manufacturer enumeration: 0=Not Selected, 1=Type X, 2=Type S.
| TRUE | PARAMS_DINT | n_PAR_PumpType.CurrentValue |  | n_PAR_PumpType.CurrentValue | Sets the pump manufacturer. Important for estimated flow due to different flow curves. Enumerated value: 0="Not Selected", 1="Type X", 2="Type S". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpType.Implemented | 31 | n_PAR_PumpType.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_PumpType.Maximum |  | n_PAR_PumpType.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_PumpType.Minimum |  | n_PAR_PumpType.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_PumpType.RemoteWriteAccess | 31 | n_PAR_PumpType.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_PumpType.RemoteValue |  | n_PAR_PumpType.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PostMoldPurgeBleedDown |  | n_PAR_PostMoldPurgeBleedDown | How long to leave the cooling valve open after the mold purge is complete to bleed out residual pressure.
| TRUE | PARAMS_DINT | n_PAR_PostMoldPurgeBleedDown.CurrentValue | 8 | n_PAR_PostMoldPurgeBleedDown.CurrentValue | Time cooling valve should remain open after mold purge is complete to bleed out residual pressure. This is the current value for this parameter used in operation of the unit. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PostMoldPurgeBleedDown.Implemented | 31 | n_PAR_PostMoldPurgeBleedDown.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_PostMoldPurgeBleedDown.Maximum | 8 | n_PAR_PostMoldPurgeBleedDown.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_PostMoldPurgeBleedDown.Minimum | 8 | n_PAR_PostMoldPurgeBleedDown.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_PostMoldPurgeBleedDown.RemoteWriteAccess | 31 | n_PAR_PostMoldPurgeBleedDown.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_PostMoldPurgeBleedDown.RemoteValue | 8 | n_PAR_PostMoldPurgeBleedDown.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_BankingInstalled |  | b_PAR_BankingInstalled | Determines if the ability to do multi-unit banking is permitted.
| TRUE | PARAMS_BOOL | b_PAR_BankingInstalled.CurrentValue |  | b_PAR_BankingInstalled.CurrentValue | Is the ability to do multi-unit banking permitted? Enumerated value: FALSE=Banking Not Permitted; TRUE=Banking Permitted. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_BankingInstalled.Implemented | 31 | b_PAR_BankingInstalled.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_BankingInstalled.RemoteWriteAccess | 31 | b_PAR_BankingInstalled.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_BankingInstalled.RemoteValue | 31 | b_PAR_BankingInstalled.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankingNodes |  | n_PAR_BankingNodes | Number of units in the bank (including the master).
| TRUE | PARAMS_DINT | n_PAR_BankingNodes.CurrentValue |  | n_PAR_BankingNodes.CurrentValue | Number of units in the bank (including the master). This is the current value for this parameter used in operation of the unit. In units of units. | units | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankingNodes.Implemented | 31 | n_PAR_BankingNodes.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_BankingNodes.Maximum |  | n_PAR_BankingNodes.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | units
| TRUE | PARAMS_DINT | n_PAR_BankingNodes.Minimum |  | n_PAR_BankingNodes.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | units
| TRUE | PARAMS_DINT | n_PAR_BankingNodes.RemoteWriteAccess | 31 | n_PAR_BankingNodes.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_BankingNodes.RemoteValue |  | n_PAR_BankingNodes.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | units | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankAlarmsAction |  | n_PAR_BankAlarmsAction | Determines how the master should inherit warnings or alarms from the slaves in the bank.
| TRUE | PARAMS_DINT | n_PAR_BankAlarmsAction.CurrentValue |  | n_PAR_BankAlarmsAction.CurrentValue | Determines how the master should inherit warnings or alarms from the slaves in the bank. Enumerated value: 0="Inherit nothing", 1="Inherit Remote Warnings Only", 2="Inherit Remote Alarms Only", 3="Inherit Both Remote Warnings and Alarms".. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankAlarmsAction.Implemented | 31 | n_PAR_BankAlarmsAction.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_BankAlarmsAction.Maximum |  | n_PAR_BankAlarmsAction.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_BankAlarmsAction.Minimum |  | n_PAR_BankAlarmsAction.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_BankAlarmsAction.RemoteWriteAccess | 31 | n_PAR_BankAlarmsAction.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_BankAlarmsAction.RemoteValue |  | n_PAR_BankAlarmsAction.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankingPollInterval |  | n_PAR_BankingPollInterval | How often to poll the bank slaves for status and update their operations.
| TRUE | PARAMS_DINT | n_PAR_BankingPollInterval.CurrentValue | 7 | n_PAR_BankingPollInterval.CurrentValue | How often to poll the bank slaves for status and update their operations. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankingPollInterval.Implemented | 31 | n_PAR_BankingPollInterval.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_BankingPollInterval.Maximum | 7 | n_PAR_BankingPollInterval.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_BankingPollInterval.Minimum | 7 | n_PAR_BankingPollInterval.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_BankingPollInterval.RemoteWriteAccess | 31 | n_PAR_BankingPollInterval.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_BankingPollInterval.RemoteValue | 7 | n_PAR_BankingPollInterval.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankedPumpStartupInterval |  | n_PAR_BankedPumpStartupInterval | Interval between sequential pump starts in a bank.
| TRUE | PARAMS_DINT | n_PAR_BankedPumpStartupInterval.CurrentValue | 7 | n_PAR_BankedPumpStartupInterval.CurrentValue | Interval between sequential pump starts in a bank. This is the current value for this parameter used in operation of the unit. In units of milliseconds. | milliseconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_BankedPumpStartupInterval.Implemented | 31 | n_PAR_BankedPumpStartupInterval.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_BankedPumpStartupInterval.Maximum | 7 | n_PAR_BankedPumpStartupInterval.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_BankedPumpStartupInterval.Minimum | 7 | n_PAR_BankedPumpStartupInterval.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | milliseconds
| TRUE | PARAMS_DINT | n_PAR_BankedPumpStartupInterval.RemoteWriteAccess | 31 | n_PAR_BankedPumpStartupInterval.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_BankedPumpStartupInterval.RemoteValue | 7 | n_PAR_BankedPumpStartupInterval.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | milliseconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeatDistributedPowerMode |  | n_PAR_HeatDistributedPowerMode | How to sequence/time heating operations across a bank of units.
| TRUE | PARAMS_DINT | n_PAR_HeatDistributedPowerMode.CurrentValue |  | n_PAR_HeatDistributedPowerMode.CurrentValue | How to sequence/time heating operations across a bank of units. Enumerated value: 0="Equally Shared, Inverted Timebases", 1="Equally Shared, NonInverted Timebases", 2="Progressive, Sequential Leader", 3="Progressive, First Unit Leading", 4="Progressive, Last Unit Leading".. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_HeatDistributedPowerMode.Implemented | 31 | n_PAR_HeatDistributedPowerMode.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_HeatDistributedPowerMode.Maximum |  | n_PAR_HeatDistributedPowerMode.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeatDistributedPowerMode.Minimum |  | n_PAR_HeatDistributedPowerMode.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_HeatDistributedPowerMode.RemoteWriteAccess | 31 | n_PAR_HeatDistributedPowerMode.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_HeatDistributedPowerMode.RemoteValue |  | n_PAR_HeatDistributedPowerMode.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CoolDistributedPowerMode |  | n_PAR_CoolDistributedPowerMode | How to sequence/time cooling operations across a bank of units.
| TRUE | PARAMS_DINT | n_PAR_CoolDistributedPowerMode.CurrentValue |  | n_PAR_CoolDistributedPowerMode.CurrentValue | How to sequence/time cooling operations across a bank of units. Enumerated value: 0="Equally Shared" (mod valve), 0="Equally Shared, Inverted Timebases" (solenoid valve), 1="Equally Shared, NonInverted Timebases" (solenoid valve only), 2="Progressive, Sequential Leader", 3="Progressive, First Unit Leading", 4="Progressive, Last Unit Leading". | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_CoolDistributedPowerMode.Implemented | 31 | n_PAR_CoolDistributedPowerMode.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_CoolDistributedPowerMode.Maximum |  | n_PAR_CoolDistributedPowerMode.Maximum | The maximum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_CoolDistributedPowerMode.Minimum |  | n_PAR_CoolDistributedPowerMode.Minimum | The minimum permitted enumerated value of .CurrentValue or .RemoteValue. | <enumeration>
| TRUE | PARAMS_DINT | n_PAR_CoolDistributedPowerMode.RemoteWriteAccess | 31 | n_PAR_CoolDistributedPowerMode.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_CoolDistributedPowerMode.RemoteValue |  | n_PAR_CoolDistributedPowerMode.RemoteValue | To change .CurrentValue remotely, write enumerated value here if .RemoteWriteAccess is TRUE. | <enumeration> | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpRepetitiveStartDelay |  | n_PAR_PumpRepetitiveStartDelay | How long to wait between repetitive starts of the pump motor.
| TRUE | PARAMS_DINT | n_PAR_PumpRepetitiveStartDelay.CurrentValue | 8 | n_PAR_PumpRepetitiveStartDelay.CurrentValue | How long to wait between repetitive starts of the pump motor. This is the current value for this parameter used in operation of the unit. | seconds | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_DINT | n_PAR_PumpRepetitiveStartDelay.Implemented | 31 | n_PAR_PumpRepetitiveStartDelay.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_DINT | n_PAR_PumpRepetitiveStartDelay.Maximum | 8 | n_PAR_PumpRepetitiveStartDelay.Maximum | The maximum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_PumpRepetitiveStartDelay.Minimum | 8 | n_PAR_PumpRepetitiveStartDelay.Minimum | The minimum permitted value of .CurrentValue or .RemoteValue. | seconds
| TRUE | PARAMS_DINT | n_PAR_PumpRepetitiveStartDelay.RemoteWriteAccess | 31 | n_PAR_PumpRepetitiveStartDelay.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_DINT | n_PAR_PumpRepetitiveStartDelay.RemoteValue | 8 | n_PAR_PumpRepetitiveStartDelay.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | seconds | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoMoldPurge |  | b_PAR_EnableAutoMoldPurge | Enables automatic mold purging upon shutdown.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoMoldPurge.CurrentValue |  | b_PAR_EnableAutoMoldPurge.CurrentValue | Mold purge cycle is automatically performed upon receiving a STOP signal. If b_PAR_EnableAutoCooldown is also enabled, it will occur first, then mold purge. Enumerated value: FALSE=Mold Purge At Shutdown Not Enabled; TRUE=Mold Purge At Shutdown Enabled. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoMoldPurge.Implemented | 31 | b_PAR_EnableAutoMoldPurge.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoMoldPurge.RemoteWriteAccess | 31 | b_PAR_EnableAutoMoldPurge.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoMoldPurge.RemoteValue | 31 | b_PAR_EnableAutoMoldPurge.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoCooldown |  | b_PAR_EnableAutoCooldown | Enables automatic cooldown upon shutdown.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoCooldown.CurrentValue |  | b_PAR_EnableAutoCooldown.CurrentValue | Cooldown cycle is automatically performed upon receiving a STOP signal. Enumerated value: FALSE=Auto Cool Stop At Shutdown Not Enabled; TRUE=Auto Cool Stop At Shutdown Enabled. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoCooldown.Implemented | 31 | b_PAR_EnableAutoCooldown.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoCooldown.RemoteWriteAccess | 31 | b_PAR_EnableAutoCooldown.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_EnableAutoCooldown.RemoteValue | 31 | b_PAR_EnableAutoCooldown.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_OEM_Product |  | b_PAR_OEM_Product | Hides logo and all traces of branding for OEM use.
| TRUE | PARAMS_BOOL | b_PAR_OEM_Product.CurrentValue |  | b_PAR_OEM_Product.CurrentValue | Hides logo and all traces of branding for OEM use. Enumerated value: FALSE=Not an OEM product; TRUE=It is an OEM product.. | <enumeration> | Parameter .Value is only valid if .Implemented is TRUE.
| TRUE | PARAMS_BOOL | b_PAR_OEM_Product.Implemented | 31 | b_PAR_OEM_Product.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_BOOL | b_PAR_OEM_Product.RemoteWriteAccess | 31 | b_PAR_OEM_Product.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_BOOL | b_PAR_OEM_Product.RemoteValue | 31 | b_PAR_OEM_Product.RemoteValue | To change .CurrentValue remotely, write value here if .RemoteWriteAccess is TRUE. | Yes/No | To change remotely, write here if .RemoteWriteAccess is TRUE.
Analog Calibration Parameters
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve |  | r_PARS_ModulatingCoolingValve | Provides the analog scaling conversion between the % open command from the controller and the actual voltage signal transmitted to the modulating valve.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.CurrentValueX1 | 11 | r_PARS_ModulatingCoolingValve.CurrentValueX1 | Controller-produced % open that will correspond to the voltage given by Y1, in units of percent (%). | % | Parameter Value X1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.CurrentValueX2 | 11 | r_PARS_ModulatingCoolingValve.CurrentValueX2 | Controller-produced %-open that will correspond to the voltage given by Y2, in units of percent (%). | % | Parameter Value X2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.CurrentValueY1 | 22 | r_PARS_ModulatingCoolingValve.CurrentValueY1 | The voltage output that corresponds to the % open amount given by X1, in units of volts (V). | V | Parameter Value Y1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.CurrentValueY2 | 22 | r_PARS_ModulatingCoolingValve.CurrentValueY2 | The voltage output that corresponds to the % open amount given by X2, in units of volts (V). | V | Parameter Value Y2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.Implemented | 31 | r_PARS_ModulatingCoolingValve.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MaximumX1 | 11 | r_PARS_ModulatingCoolingValve.MaximumX1 | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of percent (%). | %
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MaximumX2 | 11 | r_PARS_ModulatingCoolingValve.MaximumX2 | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of percent (%). | %
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MaximumY1 | 22 | r_PARS_ModulatingCoolingValve.MaximumY1 | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V). | V
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MaximumY2 | 22 | r_PARS_ModulatingCoolingValve.MaximumY2 | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V). | V
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MinimumX1 | 11 | r_PARS_ModulatingCoolingValve.MinimumX1 | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of percent (%). | %
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MinimumX2 | 11 | r_PARS_ModulatingCoolingValve.MinimumX2 | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of percent (%). | %
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MinimumY1 | 22 | r_PARS_ModulatingCoolingValve.MinimumY1 | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V). | V
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.MinimumY2 | 22 | r_PARS_ModulatingCoolingValve.MinimumY2 | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V). | V
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.RemoteWriteAccess | 31 | r_PARS_ModulatingCoolingValve.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.RemoteValueX1 | 11 | r_PARS_ModulatingCoolingValve.RemoteValueX1 | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of percent (%). | % | To change remotely, write X1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.RemoteValueX2 | 11 | r_PARS_ModulatingCoolingValve.RemoteValueX2 | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of percent (%). | % | To change remotely, write X2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.RemoteValueY1 | 22 | r_PARS_ModulatingCoolingValve.RemoteValueY1 | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of volts (V). | V | To change remotely, write Y1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ModulatingCoolingValve.RemoteValueY2 | 22 | r_PARS_ModulatingCoolingValve.RemoteValueY2 | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of volts (V). | V | To change remotely, write Y2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure |  | r_PARS_SupplyPressure | Provides the analog scaling conversion between the actual current transmitted from the To Process (supply) pressure transducer and the interpreted psi in the controller.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.CurrentValueX1 | 23 | r_PARS_SupplyPressure.CurrentValueX1 | Transducer-produced current that will correspond to the pressure given by Y1, in units of milliamps (mA). | mA | Parameter Value X1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.CurrentValueX2 | 23 | r_PARS_SupplyPressure.CurrentValueX2 | Transducer-produced current that will correspond to the pressure given by Y2, in units of milliamps (mA). | mA | Parameter Value X2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.CurrentValueY1 | 13 | r_PARS_SupplyPressure.CurrentValueY1 | Pressure that will correspond to the current specified by X1, in units of pounds per square inch (psi). | psi | Parameter Value Y1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.CurrentValueY2 | 13 | r_PARS_SupplyPressure.CurrentValueY2 | Pressure that will correspond to the current specified by X2, in units of pounds per square inch (psi). | psi | Parameter Value Y2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.Implemented | 31 | r_PARS_SupplyPressure.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MaximumX1 | 23 | r_PARS_SupplyPressure.MaximumX1 | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MaximumX2 | 23 | r_PARS_SupplyPressure.MaximumX2 | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MaximumY1 | 13 | r_PARS_SupplyPressure.MaximumY1 | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MaximumY2 | 13 | r_PARS_SupplyPressure.MaximumY2 | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MinimumX1 | 23 | r_PARS_SupplyPressure.MinimumX1 | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MinimumX2 | 23 | r_PARS_SupplyPressure.MinimumX2 | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MinimumY1 | 13 | r_PARS_SupplyPressure.MinimumY1 | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.MinimumY2 | 13 | r_PARS_SupplyPressure.MinimumY2 | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.RemoteWriteAccess | 31 | r_PARS_SupplyPressure.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.RemoteValueX1 | 23 | r_PARS_SupplyPressure.RemoteValueX1 | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA | To change remotely, write X1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.RemoteValueX2 | 23 | r_PARS_SupplyPressure.RemoteValueX2 | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA | To change remotely, write X2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.RemoteValueY1 | 13 | r_PARS_SupplyPressure.RemoteValueY1 | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi | To change remotely, write Y1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_SupplyPressure.RemoteValueY2 | 13 | r_PARS_SupplyPressure.RemoteValueY2 | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi | To change remotely, write Y2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure |  | r_PARS_ReturnPressure | Provides the analog scaling conversion between the actual current transmitted from the From Process (return) pressure transducer and the interpreted psi in the controller.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.CurrentValueX1 | 23 | r_PARS_ReturnPressure.CurrentValueX1 | Transducer-produced current that will correspond to the pressure given by Y1, in units of milliamps (mA). | mA | Parameter Value X1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.CurrentValueX2 | 23 | r_PARS_ReturnPressure.CurrentValueX2 | Transducer-produced current that will correspond to the pressure given by Y2, in units of milliamps (mA). | mA | Parameter Value X2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.CurrentValueY1 | 13 | r_PARS_ReturnPressure.CurrentValueY1 | Pressure that will correspond to the current specified by X1, in units of pounds per square inch (psi). | psi | Parameter Value Y1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.CurrentValueY2 | 13 | r_PARS_ReturnPressure.CurrentValueY2 | Pressure that will correspond to the current specified by X2, in units of pounds per square inch (psi). | psi | Parameter Value Y2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.Implemented | 31 | r_PARS_ReturnPressure.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MaximumX1 | 23 | r_PARS_ReturnPressure.MaximumX1 | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MaximumX2 | 23 | r_PARS_ReturnPressure.MaximumX2 | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MaximumY1 | 13 | r_PARS_ReturnPressure.MaximumY1 | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MaximumY2 | 13 | r_PARS_ReturnPressure.MaximumY2 | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MinimumX1 | 23 | r_PARS_ReturnPressure.MinimumX1 | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MinimumX2 | 23 | r_PARS_ReturnPressure.MinimumX2 | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of milliamps (mA). | mA
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MinimumY1 | 13 | r_PARS_ReturnPressure.MinimumY1 | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.MinimumY2 | 13 | r_PARS_ReturnPressure.MinimumY2 | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of pounds per square inch (psi). | psi
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.RemoteWriteAccess | 31 | r_PARS_ReturnPressure.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.RemoteValueX1 | 23 | r_PARS_ReturnPressure.RemoteValueX1 | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA | To change remotely, write X1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.RemoteValueX2 | 23 | r_PARS_ReturnPressure.RemoteValueX2 | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of milliamps (mA). | mA | To change remotely, write X2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.RemoteValueY1 | 13 | r_PARS_ReturnPressure.RemoteValueY1 | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi | To change remotely, write Y1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_ReturnPressure.RemoteValueY2 | 13 | r_PARS_ReturnPressure.RemoteValueY2 | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of pounds per square inch (psi). | psi | To change remotely, write Y2 here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint |  | r_PARS_AnalogSetpoint | Provides the analog scaling conversion between the actual voltage/current transmitted from the from the remote setpoint signal and the interpreted degrees of temperature in the controller.
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.CurrentValueX1 | 36 | r_PARS_AnalogSetpoint.CurrentValueX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.CurrentValueX2 | 36 | r_PARS_AnalogSetpoint.CurrentValueX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.CurrentValueY1 | 13 | r_PARS_AnalogSetpoint.CurrentValueY1 | Not currently implemented. | psi | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.CurrentValueY2 | 13 | r_PARS_AnalogSetpoint.CurrentValueY2 | Not currently implemented. | psi | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.Implemented | 31 | r_PARS_AnalogSetpoint.Implemented | Not currently implemented. | Yes/No | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MaximumX1 | 36 | r_PARS_AnalogSetpoint.MaximumX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MaximumX2 | 36 | r_PARS_AnalogSetpoint.MaximumX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MaximumY1 | 13 | r_PARS_AnalogSetpoint.MaximumY1 | Not currently implemented. | psi | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MaximumY2 | 13 | r_PARS_AnalogSetpoint.MaximumY2 | Not currently implemented. | psi | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MinimumX1 | 36 | r_PARS_AnalogSetpoint.MinimumX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MinimumX2 | 36 | r_PARS_AnalogSetpoint.MinimumX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MinimumY1 | 13 | r_PARS_AnalogSetpoint.MinimumY1 | Not currently implemented. | psi | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.MinimumY2 | 13 | r_PARS_AnalogSetpoint.MinimumY2 | Not currently implemented. | psi | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.RemoteWriteAccess | 31 | r_PARS_AnalogSetpoint.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.RemoteValueX1 | 36 | r_PARS_AnalogSetpoint.RemoteValueX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.RemoteValueX2 | 36 | r_PARS_AnalogSetpoint.RemoteValueX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.RemoteValueY1 | 13 | r_PARS_AnalogSetpoint.RemoteValueY1 | Not currently implemented. | psi | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogSetpoint.RemoteValueY2 | 13 | r_PARS_AnalogSetpoint.RemoteValueY2 | Not currently implemented. | psi | Not currently implemented
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit |  | r_PARS_AnalogProcessRetransmit | Provides the analog scaling conversion between the measured degrees of temperature in the controler and the actual voltage/current signal being transmitted to the remote equipment.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.CurrentValueX1 | 2 | r_PARS_AnalogProcessRetransmit.CurrentValueX1 | Controller-measured temperature that will correspond to the voltage/current given by Y1, in units of degrees Celsius (°C). | °C | Parameter Value X1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.CurrentValueX2 | 2 | r_PARS_AnalogProcessRetransmit.CurrentValueX2 | Controller-measured temperature that will correspond to the voltage/current given by Y2, in units of degrees Celsius (°C). | °C | Parameter Value X2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.CurrentValueY1 | 36 | r_PARS_AnalogProcessRetransmit.CurrentValueY1 | The voltage/current output that corresponds to the temperature specified by X1, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA | Parameter Value Y1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.CurrentValueY2 | 36 | r_PARS_AnalogProcessRetransmit.CurrentValueY2 | The voltage/current output that corresponds to the temperature specified by X2, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA | Parameter Value Y2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.Implemented | 31 | r_PARS_AnalogProcessRetransmit.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MaximumX1 | 2 | r_PARS_AnalogProcessRetransmit.MaximumX1 | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of degrees Celsius (°C). | °C
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MaximumX2 | 2 | r_PARS_AnalogProcessRetransmit.MaximumX2 | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of degrees Celsius (°C). | °C
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MaximumY1 | 36 | r_PARS_AnalogProcessRetransmit.MaximumY1 | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MaximumY2 | 36 | r_PARS_AnalogProcessRetransmit.MaximumY2 | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MinimumX1 | 2 | r_PARS_AnalogProcessRetransmit.MinimumX1 | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of degrees Celsius (°C). | °C
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MinimumX2 | 2 | r_PARS_AnalogProcessRetransmit.MinimumX2 | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of degrees Celsius (°C). | °C
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MinimumY1 | 36 | r_PARS_AnalogProcessRetransmit.MinimumY1 | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.MinimumY2 | 36 | r_PARS_AnalogProcessRetransmit.MinimumY2 | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.RemoteWriteAccess | 31 | r_PARS_AnalogProcessRetransmit.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.RemoteValueX1 | 2 | r_PARS_AnalogProcessRetransmit.RemoteValueX1 | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of degrees Celsius (°C). | °C | To change remotely, write X1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.RemoteValueX2 | 2 | r_PARS_AnalogProcessRetransmit.RemoteValueX2 | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of degrees Celsius (°C). | °C | To change remotely, write X2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.RemoteValueY1 | 36 | r_PARS_AnalogProcessRetransmit.RemoteValueY1 | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA | To change remotely, write Y1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogProcessRetransmit.RemoteValueY2 | 36 | r_PARS_AnalogProcessRetransmit.RemoteValueY2 | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to output selection type. | V or mA | To change remotely, write Y2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter |  | r_PARS_AnalogFlowMeter | Provides the analog scaling conversion between the actual current/voltage transmitted from the flow meter and the interpreted flowrate in the controller.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.CurrentValueX1 | 36 | r_PARS_AnalogFlowMeter.CurrentValueX1 | Flowmeter-produced voltage/current that will correspond to the flowrate given by Y1, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA | Parameter Value X1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.CurrentValueX2 | 36 | r_PARS_AnalogFlowMeter.CurrentValueX2 | Flowmeter-produced voltage/current that will correspond to the flowrate given by Y2, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA | Parameter Value X2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.CurrentValueY1 | 5 | r_PARS_AnalogFlowMeter.CurrentValueY1 | Flowrate that will correspond to the voltage/current specified by X1, in units of gallons per minute (gpm). | gpm | Parameter Value Y1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.CurrentValueY2 | 5 | r_PARS_AnalogFlowMeter.CurrentValueY2 | Flowrate that will correspond to the voltage/current specified by X2, in units of gallons per minute (gpm). | gpm | Parameter Value Y2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.Implemented | 31 | r_PARS_AnalogFlowMeter.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MaximumX1 | 36 | r_PARS_AnalogFlowMeter.MaximumX1 | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MaximumX2 | 36 | r_PARS_AnalogFlowMeter.MaximumX2 | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MaximumY1 | 5 | r_PARS_AnalogFlowMeter.MaximumY1 | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of gallons per minute (gpm). | gpm
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MaximumY2 | 5 | r_PARS_AnalogFlowMeter.MaximumY2 | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of gallons per minute (gpm). | gpm
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MinimumX1 | 36 | r_PARS_AnalogFlowMeter.MinimumX1 | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MinimumX2 | 36 | r_PARS_AnalogFlowMeter.MinimumX2 | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MinimumY1 | 5 | r_PARS_AnalogFlowMeter.MinimumY1 | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of gallons per minute (gpm). | gpm
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.MinimumY2 | 5 | r_PARS_AnalogFlowMeter.MinimumY2 | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of gallons per minute (gpm). | gpm
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.RemoteWriteAccess | 31 | r_PARS_AnalogFlowMeter.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.RemoteValueX1 | 36 | r_PARS_AnalogFlowMeter.RemoteValueX1 | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA | To change remotely, write X1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.RemoteValueX2 | 36 | r_PARS_AnalogFlowMeter.RemoteValueX2 | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of volts (V) or milliamps (mA) according to input selection type. | V or mA | To change remotely, write X2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.RemoteValueY1 | 5 | r_PARS_AnalogFlowMeter.RemoteValueY1 | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of gallons per minute (gpm). | gpm | To change remotely, write Y1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_AnalogFlowMeter.RemoteValueY2 | 5 | r_PARS_AnalogFlowMeter.RemoteValueY2 | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of gallons per minute (gpm). | gpm | To change remotely, write Y2 here if .RemoteWriteAccess is TRUE.
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput |  | r_PARS_AnalogProcessInput | Provides the analog scaling conversion between the actual voltage/current transmitted from the from the remote process signal and the interpreted degrees of temperature in the controller.
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.CurrentValueX1 | 36 | r_PARS_AnalogProcessInput.CurrentValueX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.CurrentValueX2 | 36 | r_PARS_AnalogProcessInput.CurrentValueX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.CurrentValueY1 | 2 | r_PARS_AnalogProcessInput.CurrentValueY1 | Not currently implemented. | °C | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.CurrentValueY2 | 2 | r_PARS_AnalogProcessInput.CurrentValueY2 | Not currently implemented. | °C | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.Implemented | 31 | r_PARS_AnalogProcessInput.Implemented | Not currently implemented. | Yes/No | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MaximumX1 | 36 | r_PARS_AnalogProcessInput.MaximumX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MaximumX2 | 36 | r_PARS_AnalogProcessInput.MaximumX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MaximumY1 | 2 | r_PARS_AnalogProcessInput.MaximumY1 | Not currently implemented. | °C | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MaximumY2 | 2 | r_PARS_AnalogProcessInput.MaximumY2 | Not currently implemented. | °C | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MinimumX1 | 36 | r_PARS_AnalogProcessInput.MinimumX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MinimumX2 | 36 | r_PARS_AnalogProcessInput.MinimumX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MinimumY1 | 2 | r_PARS_AnalogProcessInput.MinimumY1 | Not currently implemented. | °C | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.MinimumY2 | 2 | r_PARS_AnalogProcessInput.MinimumY2 | Not currently implemented. | °C | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.RemoteWriteAccess | 31 | r_PARS_AnalogProcessInput.RemoteWriteAccess | Not currently implemented. | Yes/No | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.RemoteValueX1 | 36 | r_PARS_AnalogProcessInput.RemoteValueX1 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.RemoteValueX2 | 36 | r_PARS_AnalogProcessInput.RemoteValueX2 | Not currently implemented. | V or mA | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.RemoteValueY1 | 2 | r_PARS_AnalogProcessInput.RemoteValueY1 | Not currently implemented. | °C | Not currently implemented
| FALSE | PARAMS_ANA | r_PARS_AnalogProcessInput.RemoteValueY2 | 2 | r_PARS_AnalogProcessInput.RemoteValueY2 | Not currently implemented. | °C | Not currently implemented
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl |  | r_PARS_RemoteResistorControl | Provides the analog scaling conversion between the actual resistance present in the remote signal and the interpreted ohms of resistance in the controller.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.CurrentValueX1 | 37 | r_PARS_RemoteResistorControl.CurrentValueX1 | Controller-measured resistance that will correspond to the controller-interpreted resistance given by Y1, in units of ohms (Ω). | Ω | Parameter Value X1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.CurrentValueX2 | 37 | r_PARS_RemoteResistorControl.CurrentValueX2 | Controller-measured resistance that will correspond to the controller-interpreted resistance given by Y2, in units of ohms (Ω). | Ω | Parameter Value X2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.CurrentValueY1 | 37 | r_PARS_RemoteResistorControl.CurrentValueY1 | Actual resistance that will correspond to the controller-measured resistance specified by X1, in units of ohms (Ω). | Ω | Parameter Value Y1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.CurrentValueY2 | 37 | r_PARS_RemoteResistorControl.CurrentValueY2 | Actual resistance that will correspond to the controller-measured resistance specified by X2, in units of ohms (Ω). | Ω | Parameter Value Y2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.Implemented | 31 | r_PARS_RemoteResistorControl.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MaximumX1 | 37 | r_PARS_RemoteResistorControl.MaximumX1 | The maximum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MaximumX2 | 37 | r_PARS_RemoteResistorControl.MaximumX2 | The maximum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MaximumY1 | 37 | r_PARS_RemoteResistorControl.MaximumY1 | The maximum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MaximumY2 | 37 | r_PARS_RemoteResistorControl.MaximumY2 | The maximum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MinimumX1 | 37 | r_PARS_RemoteResistorControl.MinimumX1 | The minimum permitted value of .CurrentValueX1 or .RemoteValueX1, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MinimumX2 | 37 | r_PARS_RemoteResistorControl.MinimumX2 | The minimum permitted value of .CurrentValueX2 or .RemoteValueX2, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MinimumY1 | 37 | r_PARS_RemoteResistorControl.MinimumY1 | The minimum permitted value of .CurrentValueY1 or .RemoteValueY1, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.MinimumY2 | 37 | r_PARS_RemoteResistorControl.MinimumY2 | The minimum permitted value of .CurrentValueY2 or .RemoteValueY2, in units of ohms (Ω). | Ω
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.RemoteWriteAccess | 31 | r_PARS_RemoteResistorControl.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | Yes/No | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.RemoteValueX1 | 37 | r_PARS_RemoteResistorControl.RemoteValueX1 | To change remotely, write .CurrentValueX1 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω | To change remotely, write X1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.RemoteValueX2 | 37 | r_PARS_RemoteResistorControl.RemoteValueX2 | To change remotely, write .CurrentValueX2 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω | To change remotely, write X2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.RemoteValueY1 | 37 | r_PARS_RemoteResistorControl.RemoteValueY1 | To change remotely, write .CurrentValueY1 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω | To change remotely, write Y1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_ANA | r_PARS_RemoteResistorControl.RemoteValueY2 | 37 | r_PARS_RemoteResistorControl.RemoteValueY2 | To change remotely, write .CurrentValueY2 here if .RemoteWriteAccess is TRUE, in units of ohms (Ω). | Ω | To change remotely, write Y2 here if .RemoteWriteAccess is TRUE.
Networking Parameters
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress |  | n_PAR_IpAddress | IP address for the ethenet network.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.CurrentValue[1] |  | n_PAR_IpAddress.CurrentValue[1] | IP address octet #1 for the ethenet network. | N/A | Parameter Octet #1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.CurrentValue[2] |  | n_PAR_IpAddress.CurrentValue[2] | IP address octet #2 for the ethenet network. | N/A | Parameter Octet #2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.CurrentValue[3] |  | n_PAR_IpAddress.CurrentValue[3] | IP address octet #3 for the ethenet network. | N/A | Parameter Octet #3. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.CurrentValue[4] |  | n_PAR_IpAddress.CurrentValue[4] | IP address octet #4 for the ethenet network. | N/A | Parameter Octet #4. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.Implemented | 31 | n_PAR_IpAddress.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.RemoteWriteAccess |  | n_PAR_IpAddress.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | N/A | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.RemoteValue[1] |  | n_PAR_IpAddress.RemoteValue[1] | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.RemoteValue[2] |  | n_PAR_IpAddress.RemoteValue[2] | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.RemoteValue[3] |  | n_PAR_IpAddress.RemoteValue[3] | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_IpAddress.RemoteValue[4] |  | n_PAR_IpAddress.RemoteValue[4] | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet |  | n_PAR_Subnet | Subnet mask for the ethenet network.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.CurrentValue[1] |  | n_PAR_Subnet.CurrentValue[1] | Subnet mask octet #1 for the ethenet network. | N/A | Parameter Octet #1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.CurrentValue[2] |  | n_PAR_Subnet.CurrentValue[2] | Subnet mask octet #2 for the ethenet network. | N/A | Parameter Octet #2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.CurrentValue[3] |  | n_PAR_Subnet.CurrentValue[3] | Subnet mask octet #3 for the ethenet network. | N/A | Parameter Octet #3. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.CurrentValue[4] |  | n_PAR_Subnet.CurrentValue[4] | Subnet mask octet #4 for the ethenet network. | N/A | Parameter Octet #4. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.Implemented | 31 | n_PAR_Subnet.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.RemoteWriteAccess |  | n_PAR_Subnet.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | N/A | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.RemoteValue[1] |  | n_PAR_Subnet.RemoteValue[1] | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.RemoteValue[2] |  | n_PAR_Subnet.RemoteValue[2] | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.RemoteValue[3] |  | n_PAR_Subnet.RemoteValue[3] | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Subnet.RemoteValue[4] |  | n_PAR_Subnet.RemoteValue[4] | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway |  | n_PAR_Gateway | Gateway for the ethenet network.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.CurrentValue[1] |  | n_PAR_Gateway.CurrentValue[1] | Gateway octet #1 for the ethenet network. | N/A | Parameter Octet #1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.CurrentValue[2] |  | n_PAR_Gateway.CurrentValue[2] | Gateway octet #2 for the ethenet network. | N/A | Parameter Octet #2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.CurrentValue[3] |  | n_PAR_Gateway.CurrentValue[3] | Gateway octet #3 for the ethenet network. | N/A | Parameter Octet #3. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.CurrentValue[4] |  | n_PAR_Gateway.CurrentValue[4] | Gateway octet #4 for the ethenet network. | N/A | Parameter Octet #4. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.Implemented | 31 | n_PAR_Gateway.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.RemoteWriteAccess |  | n_PAR_Gateway.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | N/A | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.RemoteValue[1] |  | n_PAR_Gateway.RemoteValue[1] | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.RemoteValue[2] |  | n_PAR_Gateway.RemoteValue[2] | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.RemoteValue[3] |  | n_PAR_Gateway.RemoteValue[3] | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_Gateway.RemoteValue[4] |  | n_PAR_Gateway.RemoteValue[4] | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1 |  | n_PAR_DnsAddress1 | DNS server #1 IP address for the ethenet network.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.CurrentValue[1] |  | n_PAR_DnsAddress1.CurrentValue[1] | DNS server #1 IP address octet #1 for the ethenet network. | N/A | Parameter Octet #1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.CurrentValue[2] |  | n_PAR_DnsAddress1.CurrentValue[2] | DNS server #1 IP address octet #2 for the ethenet network. | N/A | Parameter Octet #2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.CurrentValue[3] |  | n_PAR_DnsAddress1.CurrentValue[3] | DNS server #1 IP address octet #3 for the ethenet network. | N/A | Parameter Octet #3. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.CurrentValue[4] |  | n_PAR_DnsAddress1.CurrentValue[4] | DNS server #1 IP address octet #4 for the ethenet network. | N/A | Parameter Octet #4. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.Implemented | 31 | n_PAR_DnsAddress1.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.RemoteWriteAccess |  | n_PAR_DnsAddress1.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | N/A | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.RemoteValue[1] |  | n_PAR_DnsAddress1.RemoteValue[1] | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.RemoteValue[2] |  | n_PAR_DnsAddress1.RemoteValue[2] | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.RemoteValue[3] |  | n_PAR_DnsAddress1.RemoteValue[3] | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress1.RemoteValue[4] |  | n_PAR_DnsAddress1.RemoteValue[4] | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2 |  | n_PAR_DnsAddress2 | DNS server #2 IP address for the ethenet network.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.CurrentValue[1] |  | n_PAR_DnsAddress2.CurrentValue[1] | DNS server #2 IP address octet #1 for the ethenet network. | N/A | Parameter Octet #1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.CurrentValue[2] |  | n_PAR_DnsAddress2.CurrentValue[2] | DNS server #2 IP address octet #2 for the ethenet network. | N/A | Parameter Octet #2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.CurrentValue[3] |  | n_PAR_DnsAddress2.CurrentValue[3] | DNS server #2 IP address octet #3 for the ethenet network. | N/A | Parameter Octet #3. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.CurrentValue[4] |  | n_PAR_DnsAddress2.CurrentValue[4] | DNS server #2 IP address octet #4 for the ethenet network. | N/A | Parameter Octet #4. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.Implemented | 31 | n_PAR_DnsAddress2.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.RemoteWriteAccess |  | n_PAR_DnsAddress2.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | N/A | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.RemoteValue[1] |  | n_PAR_DnsAddress2.RemoteValue[1] | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.RemoteValue[2] |  | n_PAR_DnsAddress2.RemoteValue[2] | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.RemoteValue[3] |  | n_PAR_DnsAddress2.RemoteValue[3] | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_DnsAddress2.RemoteValue[4] |  | n_PAR_DnsAddress2.RemoteValue[4] | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress |  | n_PAR_NtpAddress | NTP server IP address for the ethenet network.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.CurrentValue[1] |  | n_PAR_NtpAddress.CurrentValue[1] | NTP server IP address octet #1 for the ethenet network. | N/A | Parameter Octet #1. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.CurrentValue[2] |  | n_PAR_NtpAddress.CurrentValue[2] | NTP server IP address octet #2 for the ethenet network. | N/A | Parameter Octet #2. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.CurrentValue[3] |  | n_PAR_NtpAddress.CurrentValue[3] | NTP server IP address octet #3 for the ethenet network. | N/A | Parameter Octet #3. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.CurrentValue[4] |  | n_PAR_NtpAddress.CurrentValue[4] | NTP server IP address octet #4 for the ethenet network. | N/A | Parameter Octet #4. Only valid if .Implemented is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.Implemented | 31 | n_PAR_NtpAddress.Implemented | Parameter .CurrentValue is only relevant/valid if .Implemented is TRUE. | Yes/No
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.RemoteWriteAccess |  | n_PAR_NtpAddress.RemoteWriteAccess | Determines if remote values will currently be accepted from .RemoteValue. | N/A | Determines if values will be accepted from .RemoteValue.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.RemoteValue[1] |  | n_PAR_NtpAddress.RemoteValue[1] | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #1 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.RemoteValue[2] |  | n_PAR_NtpAddress.RemoteValue[2] | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #2 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.RemoteValue[3] |  | n_PAR_NtpAddress.RemoteValue[3] | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #3 here if .RemoteWriteAccess is TRUE.
| TRUE | PARAMS_IPv4 | n_PAR_NtpAddress.RemoteValue[4] |  | n_PAR_NtpAddress.RemoteValue[4] | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE. | N/A | To change remotely, write Octet #4 here if .RemoteWriteAccess is TRUE.
Warnings
| TRUE | WARNINGS | b_WRN_PumpOverload |  | b_WRN_PumpOverload | The pump overload protector has tripped from too much pump motor current. This is typically caused by excessive flow in the process loop. Check the fluid loop for too much flow or restrict it. Manually reset overload protector in electrical panel.
| TRUE | WARNINGS | b_WRN_PumpOverload.Value | 38 | b_WRN_PumpOverload.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_PumpOverload.Enable | 39 | b_WRN_PumpOverload.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_PumpOverload.AutoReset | 40 | b_WRN_PumpOverload.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_PumpOverload.Count | 28 | b_WRN_PumpOverload.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_FlowmeterLowFlow |  | b_WRN_FlowmeterLowFlow | There is insufficient flow in the process loop for an extended period of time.
| TRUE | WARNINGS | b_WRN_FlowmeterLowFlow.Value | 38 | b_WRN_FlowmeterLowFlow.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_FlowmeterLowFlow.Enable | 39 | b_WRN_FlowmeterLowFlow.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_FlowmeterLowFlow.AutoReset | 40 | b_WRN_FlowmeterLowFlow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_FlowmeterLowFlow.Count | 28 | b_WRN_FlowmeterLowFlow.Count | Number of times .Value has been triggered. | Events
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Open |  | b_WRN_Failover_SupplyToReturn_SupplyRTD_Open | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Open.Value | 38 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Open.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Open.Enable | 39 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Open.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Open.AutoReset | 40 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Open.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Open.Count | 28 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Open.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Shorted |  | b_WRN_Failover_SupplyToReturn_SupplyRTD_Shorted | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Shorted.Value | 38 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Shorted.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Shorted.Enable | 39 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Shorted.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Shorted.AutoReset | 40 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Shorted.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Shorted.Count | 28 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Shorted.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Other |  | b_WRN_Failover_SupplyToReturn_SupplyRTD_Other | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Other.Value | 38 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Other.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Other.Enable | 39 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Other.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Other.AutoReset | 40 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Other.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_SupToRet_SupRTD_Other.Count | 28 | b_WRN_Failover_SupplyToReturn_SupplyRTD_Other.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Open |  | b_WRN_Failover_ReturnToSupply_ReturnRTD_Open | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Open.Value | 38 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Open.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Open.Enable | 39 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Open.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Open.AutoReset | 40 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Open.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Open.Count | 28 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Open.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Shorted |  | b_WRN_Failover_ReturnToSupply_ReturnRTD_Shorted | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Shorted.Value | 38 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Shorted.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Shorted.Enable | 39 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Shorted.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Shorted.AutoReset | 40 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Shorted.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Shorted.Count | 28 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Shorted.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Other |  | b_WRN_Failover_ReturnToSupply_ReturnRTD_Other | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Other.Value | 38 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Other.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Other.Enable | 39 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Other.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Other.AutoReset | 40 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Other.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RetToSup_RetRTD_Other.Count | 28 | b_WRN_Failover_ReturnToSupply_ReturnRTD_Other.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Open |  | b_WRN_Failover_RemoteToReturn_RemoteRTD_Open | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Open.Value | 38 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Open.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Open.Enable | 39 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Open.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Open.AutoReset | 40 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Open.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Open.Count | 28 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Open.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Shorted |  | b_WRN_Failover_RemoteToReturn_RemoteRTD_Shorted | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Shorted.Value | 38 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Shorted.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Shorted.Enable | 39 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Shorted.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Shorted.AutoReset | 40 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Shorted.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Shorted.Count | 28 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Shorted.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Other |  | b_WRN_Failover_RemoteToReturn_RemoteRTD_Other | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Other.Value | 38 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Other.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Other.Enable | 39 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Other.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Other.AutoReset | 40 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Other.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_RemToRet_RemRTD_Other.Count | 28 | b_WRN_Failover_RemoteToReturn_RemoteRTD_Other.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInHigh |  | b_WRN_Failover_AnalogToReturn_AnalogProcessInputHigh | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInHigh.Value | 38 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputHigh.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInHigh.Enable | 39 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputHigh.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInHigh.AutoReset | 40 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputHigh.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInHigh.Count | 28 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputHigh.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInLow |  | b_WRN_Failover_AnalogToReturn_AnalogProcessInputLow | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInLow.Value | 38 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputLow.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInLow.Enable | 39 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputLow.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInLow.AutoReset | 40 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputLow.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInLow.Count | 28 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputLow.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInOther |  | b_WRN_Failover_AnalogToReturn_AnalogProcessInputOther | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInOther.Value | 38 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputOther.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInOther.Enable | 39 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputOther.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInOther.AutoReset | 40 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputOther.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToRet_AnaProcInOther.Count | 28 | b_WRN_Failover_AnalogToReturn_AnalogProcessInputOther.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHigh |  | b_WRN_Failover_NetworkToReturn_NetworkProcessHigh | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHigh.Value | 38 | b_WRN_Failover_NetworkToReturn_NetworkProcessHigh.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHigh.Enable | 39 | b_WRN_Failover_NetworkToReturn_NetworkProcessHigh.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHigh.AutoReset | 40 | b_WRN_Failover_NetworkToReturn_NetworkProcessHigh.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHigh.Count | 28 | b_WRN_Failover_NetworkToReturn_NetworkProcessHigh.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcLow |  | b_WRN_Failover_NetworkToReturn_NetworkProcessLow | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcLow.Value | 38 | b_WRN_Failover_NetworkToReturn_NetworkProcessLow.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcLow.Enable | 39 | b_WRN_Failover_NetworkToReturn_NetworkProcessLow.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcLow.AutoReset | 40 | b_WRN_Failover_NetworkToReturn_NetworkProcessLow.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcLow.Count | 28 | b_WRN_Failover_NetworkToReturn_NetworkProcessLow.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHB |  | b_WRN_Failover_NetworkToReturn_NetworkProcessHB | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHB.Value | 38 | b_WRN_Failover_NetworkToReturn_NetworkProcessHB.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHB.Enable | 39 | b_WRN_Failover_NetworkToReturn_NetworkProcessHB.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHB.AutoReset | 40 | b_WRN_Failover_NetworkToReturn_NetworkProcessHB.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToRet_NetProcHB.Count | 28 | b_WRN_Failover_NetworkToReturn_NetworkProcessHB.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_High |  | b_WRN_Failover_AnalogToMain_AnalogSetpoint_High | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_High.Value | 38 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_High.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_High.Enable | 39 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_High.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_High.AutoReset | 40 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_High.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_High.Count | 28 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_High.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Low |  | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Low | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Low.Value | 38 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Low.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Low.Enable | 39 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Low.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Low.AutoReset | 40 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Low.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Low.Count | 28 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Low.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Other |  | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Other | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Other.Value | 38 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Other.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Other.Enable | 39 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Other.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Other.AutoReset | 40 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Other.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_AnaToMain_AnaSP_Other.Count | 28 | b_WRN_Failover_AnalogToMain_AnalogSetpoint_Other.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_High |  | b_WRN_Failover_NetworkToMain_NetworkSetpoint_High | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_High.Value | 38 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_High.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_High.Enable | 39 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_High.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_High.AutoReset | 40 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_High.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_High.Count | 28 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_High.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_Low |  | b_WRN_Failover_NetworkToMain_NetworkSetpoint_Low | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_Low.Value | 38 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_Low.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_Low.Enable | 39 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_Low.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_Low.AutoReset | 40 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_Low.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_Low.Count | 28 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_Low.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_HB |  | b_WRN_Failover_NetworkToMain_NetworkSetpoint_HB | Not currently enabled. |  | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_HB.Value | 38 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_HB.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_HB.Enable | 39 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_HB.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_HB.AutoReset | 40 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_HB.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | WARNINGS | b_WRN_FO_NetToMain_NetSP_HB.Count | 28 | b_WRN_Failover_NetworkToMain_NetworkSetpoint_HB.Count | Not currently enabled. | Events | Not currently enabled.
| TRUE | WARNINGS | b_WRN_PressureBelowMinimum |  | b_WRN_PressureBelowMinimum | Process fluid pressurization supply is too low or there is a leak in the process loop. Machine will automatically restart when pressure returns.
| TRUE | WARNINGS | b_WRN_PressureBelowMinimum.Value | 38 | b_WRN_PressureBelowMinimum.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_PressureBelowMinimum.Enable | 39 | b_WRN_PressureBelowMinimum.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_PressureBelowMinimum.AutoReset | 40 | b_WRN_PressureBelowMinimum.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_PressureBelowMinimum.Count | 28 | b_WRN_PressureBelowMinimum.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_PressureNotHighEnough |  | b_WRN_PressureNotHighEnough | Process loop pressure is too low for the actual high system temperature. The process loop is pressurized by the incoming cooling water, and must remain sufficient, especially at high operating temperatures. Increase the cooling water supply pressure. Operate the system at a lower temperature setpoint.
| TRUE | WARNINGS | b_WRN_PressureNotHighEnough.Value | 38 | b_WRN_PressureNotHighEnough.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_PressureNotHighEnough.Enable | 39 | b_WRN_PressureNotHighEnough.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_PressureNotHighEnough.AutoReset | 40 | b_WRN_PressureNotHighEnough.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_PressureNotHighEnough.Count | 28 | b_WRN_PressureNotHighEnough.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_SetpointTooHighForPressure |  | b_WRN_SetpointTooHighForPressure | Setpoint is too high for current system pressure. Operate the system at a lower temperature setpoint. Increase the cooling water supply pressure.
| TRUE | WARNINGS | b_WRN_SetpointTooHighForPressure.Value | 38 | b_WRN_SetpointTooHighForPressure.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_SetpointTooHighForPressure.Enable | 39 | b_WRN_SetpointTooHighForPressure.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_SetpointTooHighForPressure.AutoReset | 40 | b_WRN_SetpointTooHighForPressure.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_SetpointTooHighForPressure.Count | 28 | b_WRN_SetpointTooHighForPressure.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_SupplyRTD_Open |  | b_WRN_SupplyRTD_Open | An OPEN CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "To Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "To process" RTD circuit.
| TRUE | WARNINGS | b_WRN_SupplyRTD_Open.Value | 38 | b_WRN_SupplyRTD_Open.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_SupplyRTD_Open.Enable | 39 | b_WRN_SupplyRTD_Open.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_SupplyRTD_Open.AutoReset | 40 | b_WRN_SupplyRTD_Open.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_SupplyRTD_Open.Count | 28 | b_WRN_SupplyRTD_Open.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_SupplyRTD_Shorted |  | b_WRN_SupplyRTD_Shorted | A SHORT CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "To Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "To process" RTD circuit.
| TRUE | WARNINGS | b_WRN_SupplyRTD_Shorted.Value | 38 | b_WRN_SupplyRTD_Shorted.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_SupplyRTD_Shorted.Enable | 39 | b_WRN_SupplyRTD_Shorted.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_SupplyRTD_Shorted.AutoReset | 40 | b_WRN_SupplyRTD_Shorted.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_SupplyRTD_Shorted.Count | 28 | b_WRN_SupplyRTD_Shorted.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_SupplyRTD_Other |  | b_WRN_SupplyRTD_Other | A CHANNEL FAULT has occurred in the "To Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit.
| TRUE | WARNINGS | b_WRN_SupplyRTD_Other.Value | 38 | b_WRN_SupplyRTD_Other.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_SupplyRTD_Other.Enable | 39 | b_WRN_SupplyRTD_Other.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_SupplyRTD_Other.AutoReset | 40 | b_WRN_SupplyRTD_Other.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_SupplyRTD_Other.Count | 28 | b_WRN_SupplyRTD_Other.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_ReturnRTD_Open |  | b_WRN_ReturnRTD_Open | An OPEN CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "From Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "From process" RTD circuit.
| TRUE | WARNINGS | b_WRN_ReturnRTD_Open.Value | 38 | b_WRN_ReturnRTD_Open.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_ReturnRTD_Open.Enable | 39 | b_WRN_ReturnRTD_Open.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_ReturnRTD_Open.AutoReset | 40 | b_WRN_ReturnRTD_Open.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_ReturnRTD_Open.Count | 28 | b_WRN_ReturnRTD_Open.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_ReturnRTD_Shorted |  | b_WRN_ReturnRTD_Shorted | A SHORT CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check "From Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "From process" RTD circuit.
| TRUE | WARNINGS | b_WRN_ReturnRTD_Shorted.Value | 38 | b_WRN_ReturnRTD_Shorted.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_ReturnRTD_Shorted.Enable | 39 | b_WRN_ReturnRTD_Shorted.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_ReturnRTD_Shorted.AutoReset | 40 | b_WRN_ReturnRTD_Shorted.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_ReturnRTD_Shorted.Count | 28 | b_WRN_ReturnRTD_Shorted.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_ReturnRTD_Other |  | b_WRN_ReturnRTD_Other | A CHANNEL FAULT has occurred in the "From Process" RTD temperature probe or wiring. The failed probe is not controlling, so machine operation is not affected. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit.
| TRUE | WARNINGS | b_WRN_ReturnRTD_Other.Value | 38 | b_WRN_ReturnRTD_Other.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_ReturnRTD_Other.Enable | 39 | b_WRN_ReturnRTD_Other.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_ReturnRTD_Other.AutoReset | 40 | b_WRN_ReturnRTD_Other.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_ReturnRTD_Other.Count | 28 | b_WRN_ReturnRTD_Other.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_SupplyTransducerHigh |  | b_WRN_SupplyPressureTransducerHigh | A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. The machine can continue to operate, but will be unable to approximate flow. Check the "To Process" pressure transducer. Check the analog wiring.
| TRUE | WARNINGS | b_WRN_SupplyTransducerHigh.Value | 38 | b_WRN_SupplyPressureTransducerHigh.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_SupplyTransducerHigh.Enable | 39 | b_WRN_SupplyPressureTransducerHigh.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_SupplyTransducerHigh.AutoReset | 40 | b_WRN_SupplyPressureTransducerHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_SupplyTransducerHigh.Count | 28 | b_WRN_SupplyPressureTransducerHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_SupplyTransducerLow |  | b_WRN_SupplyPressureTransducerLow | A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. The machine can continue to operate, but will be unable to approximate flow. Check the "To Process" pressure transducer. Check the analog wiring.
| TRUE | WARNINGS | b_WRN_SupplyTransducerLow.Value | 38 | b_WRN_SupplyPressureTransducerLow.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_SupplyTransducerLow.Enable | 39 | b_WRN_SupplyPressureTransducerLow.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_SupplyTransducerLow.AutoReset | 40 | b_WRN_SupplyPressureTransducerLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_SupplyTransducerLow.Count | 28 | b_WRN_SupplyPressureTransducerLow.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_SupplyTransducerOther |  | b_WRN_SupplyPressureTransducerOther | A CHANNEL FAULT has occurred on the "To Process" pressure transducer or wiring. The machine can continue to operate, but will be unable to approximate flow. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit.
| TRUE | WARNINGS | b_WRN_SupplyTransducerOther.Value | 38 | b_WRN_SupplyPressureTransducerOther.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_SupplyTransducerOther.Enable | 39 | b_WRN_SupplyPressureTransducerOther.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_SupplyTransducerOther.AutoReset | 40 | b_WRN_SupplyPressureTransducerOther.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_SupplyTransducerOther.Count | 28 | b_WRN_SupplyPressureTransducerOther.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_AnaFlowmeterHigh |  | b_WRN_AnalogFlowmeterHigh | A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. The machine can continue to operate, but will be unable to measure flow or take action on low flow conditions. Check the flowmeter. Check the analog wiring.
| TRUE | WARNINGS | b_WRN_AnaFlowmeterHigh.Value | 38 | b_WRN_AnalogFlowmeterHigh.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_AnaFlowmeterHigh.Enable | 39 | b_WRN_AnalogFlowmeterHigh.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_AnaFlowmeterHigh.AutoReset | 40 | b_WRN_AnalogFlowmeterHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_AnaFlowmeterHigh.Count | 28 | b_WRN_AnalogFlowmeterHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_AnaFlowmeterLow |  | b_WRN_AnalogFlowmeterLow | A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. The machine can continue to operate, but will be unable to measure flow or take action on low flow conditions. Check the flowmeter. Check the analog wiring.
| TRUE | WARNINGS | b_WRN_AnaFlowmeterLow.Value | 38 | b_WRN_AnalogFlowmeterLow.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_AnaFlowmeterLow.Enable | 39 | b_WRN_AnalogFlowmeterLow.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_AnaFlowmeterLow.AutoReset | 40 | b_WRN_AnalogFlowmeterLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_AnaFlowmeterLow.Count | 28 | b_WRN_AnalogFlowmeterLow.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_AnaFlowmeterOther |  | b_WRN_AnalogFlowmeterOther | A CHANNEL FAULT has occurred on the FLOWMETER or wiring. The machine can continue to operate, but will be unable to measure flow or take action on low flow conditions. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit.
| TRUE | WARNINGS | b_WRN_AnaFlowmeterOther.Value | 38 | b_WRN_AnalogFlowmeterOther.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_AnaFlowmeterOther.Enable | 39 | b_WRN_AnalogFlowmeterOther.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_AnaFlowmeterOther.AutoReset | 40 | b_WRN_AnalogFlowmeterOther.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_AnaFlowmeterOther.Count | 28 | b_WRN_AnalogFlowmeterOther.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_FlashMemoryWrites |  | b_WRN_FlashMemoryWrites | Flash memory writes are excessive. Contact the Service department of the manufacturer.
| TRUE | WARNINGS | b_WRN_FlashMemoryWrites.Value | 38 | b_WRN_FlashMemoryWrites.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_FlashMemoryWrites.Enable | 39 | b_WRN_FlashMemoryWrites.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_FlashMemoryWrites.AutoReset | 40 | b_WRN_FlashMemoryWrites.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_FlashMemoryWrites.Count | 28 | b_WRN_FlashMemoryWrites.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_HighDeviation |  | b_WRN_HighDeviation | The temperature has deviated too high for too long above the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/blocked cooling valve. Check for a failed (stuck on) heater contactor.
| TRUE | WARNINGS | b_WRN_HighDeviation.Value | 38 | b_WRN_HighDeviation.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_HighDeviation.Enable | 39 | b_WRN_HighDeviation.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_HighDeviation.AutoReset | 40 | b_WRN_HighDeviation.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_HighDeviation.Count | 28 | b_WRN_HighDeviation.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_LowDeviation |  | b_WRN_LowDeviation | The temperature has deviated too low for too long below the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/stuck open cooling valve. Check for a failed heater contactor.
| TRUE | WARNINGS | b_WRN_LowDeviation.Value | 38 | b_WRN_LowDeviation.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_LowDeviation.Enable | 39 | b_WRN_LowDeviation.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_LowDeviation.AutoReset | 40 | b_WRN_LowDeviation.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_LowDeviation.Count | 28 | b_WRN_LowDeviation.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_NetworkHeartbeatLost |  | b_WRN_NetworkHeartbeatLost | The NETWORK HEARTBEAT HAS BEEN LOST after having been initially established. Fix network or remote node. Change Network Timeout action or timeout period.
| TRUE | WARNINGS | b_WRN_NetworkHeartbeatLost.Value | 38 | b_WRN_NetworkHeartbeatLost.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_NetworkHeartbeatLost.Enable | 39 | b_WRN_NetworkHeartbeatLost.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_NetworkHeartbeatLost.AutoReset | 40 | b_WRN_NetworkHeartbeatLost.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_NetworkHeartbeatLost.Count | 28 | b_WRN_NetworkHeartbeatLost.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_RemoteSlaveWarningActive |  | b_WRN_RemoteSlaveWarningActive | A warning has been inherrited from banked Slave unit. Rectify the warning on the banked slave unit. Change the master to not register banked slave warnings.
| TRUE | WARNINGS | b_WRN_RemoteSlaveWarningActive.Value | 38 | b_WRN_RemoteSlaveWarningActive.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_RemoteSlaveWarningActive.Enable | 39 | b_WRN_RemoteSlaveWarningActive.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_RemoteSlaveWarningActive.AutoReset | 40 | b_WRN_RemoteSlaveWarningActive.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_RemoteSlaveWarningActive.Count | 28 | b_WRN_RemoteSlaveWarningActive.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_TooManyHeaterCycles |  | b_WRN_TooManyHeaterCycles | The machine is being used in a manner that cycles the heaters too frequently. This will wear out the heater contactor prematurely, leading to early machine failure. The PID should be re-tuned. SSR-equipped model should be used for this application.
| TRUE | WARNINGS | b_WRN_TooManyHeaterCycles.Value | 38 | b_WRN_TooManyHeaterCycles.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_TooManyHeaterCycles.Enable | 39 | b_WRN_TooManyHeaterCycles.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_TooManyHeaterCycles.AutoReset | 40 | b_WRN_TooManyHeaterCycles.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_TooManyHeaterCycles.Count | 28 | b_WRN_TooManyHeaterCycles.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_WornOutHeaterContactor |  | b_WRN_WornOutHeaterContactor | The HEATER CONTACTOR is nearing the end of its operational life. Please replace the component whenever possible to eliminate this source of eventual failure. Replace the electromechanical heater contactor.
| TRUE | WARNINGS | b_WRN_WornOutHeaterContactor.Value | 38 | b_WRN_WornOutHeaterContactor.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_WornOutHeaterContactor.Enable | 39 | b_WRN_WornOutHeaterContactor.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_WornOutHeaterContactor.AutoReset | 40 | b_WRN_WornOutHeaterContactor.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_WornOutHeaterContactor.Count | 28 | b_WRN_WornOutHeaterContactor.Count | Number of times .Value has been triggered. | Events
| TRUE | WARNINGS | b_WRN_ClockNotSet |  | b_WRN_ClockNotSet | The DATE and TIME have not been set in the controller. Trends, schedules, warnings and alarms may not operate properly until this is completed. Set the DATE and TIME.
| TRUE | WARNINGS | b_WRN_ClockNotSet.Value | 38 | b_WRN_ClockNotSet.Value | This bit signifies whether or not this warning is currently active. | Inactive/Active
| TRUE | WARNINGS | b_WRN_ClockNotSet.Enable | 39 | b_WRN_ClockNotSet.Enable | If enabled, the warning is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the warning. | Disabled/Enabled
| TRUE | WARNINGS | b_WRN_ClockNotSet.AutoReset | 40 | b_WRN_ClockNotSet.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the warning would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | WARNINGS | b_WRN_ClockNotSet.Count | 28 | b_WRN_ClockNotSet.Count | Number of times .Value has been triggered. | Events
Alarms
| TRUE | ALARMS | b_ALM_IO_HMI_ConnectionFailure |  | b_ALM_IO_HMI_ConnectionFailure | The touchscreen controller has lost connection with all of the IO modules. The touchscreen and IO modules are interconnected via 2 conductors (plus shield). They are each supplied with 24VDC separately. All must be present for the system to function properly. See electrical prints for details. Verify connections at touchscreen and first IO module. Check all IO modules are powered-up/illuminated.
| TRUE | ALARMS | b_ALM_IO_HMI_ConnectionFailure.Value | 38 | b_ALM_IO_HMI_ConnectionFailure.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_IO_HMI_ConnectionFailure.Enable | 39 | b_ALM_IO_HMI_ConnectionFailure.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_IO_HMI_ConnectionFailure.AutoReset | 40 | b_ALM_IO_HMI_ConnectionFailure.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_IO_HMI_ConnectionFailure.Count | 28 | b_ALM_IO_HMI_ConnectionFailure.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_IO_ModuleLinkFailure |  | b_ALM_IO_ModuleLinkFailure | A particular IO module and all IO modules to its right have suffered a communication failure with the touchscreen. Connection on the left side of an IO module is likely bad. Check that IO modules are tightly mated to each other. Check IO modules are seated & locked on DIN rail.
| TRUE | ALARMS | b_ALM_IO_ModuleLinkFailure.Value | 38 | b_ALM_IO_ModuleLinkFailure.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_IO_ModuleLinkFailure.Enable | 39 | b_ALM_IO_ModuleLinkFailure.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_IO_ModuleLinkFailure.AutoReset | 40 | b_ALM_IO_ModuleLinkFailure.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_IO_ModuleLinkFailure.Count | 28 | b_ALM_IO_ModuleLinkFailure.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_IO_HardwareMismatch |  | b_ALM_IO_HardwareMismatch | An IO module is not the correct part number. Replace the IO module with the correct component. Check for accidental mixed-up order of IO modules.
| TRUE | ALARMS | b_ALM_IO_HardwareMismatch.Value | 38 | b_ALM_IO_HardwareMismatch.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_IO_HardwareMismatch.Enable | 39 | b_ALM_IO_HardwareMismatch.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_IO_HardwareMismatch.AutoReset | 40 | b_ALM_IO_HardwareMismatch.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_IO_HardwareMismatch.Count | 28 | b_ALM_IO_HardwareMismatch.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_IO_ModuleInternalFailure |  | b_ALM_IO_ModuleInternalFailure | IO module has an internal failure. IO modules are numbered from left to right, starting with #1 ("X20BR7300") at the leftmost position. Replace the faulty IO module. Inspect machine for root cause of IO module failure.
| TRUE | ALARMS | b_ALM_IO_ModuleInternalFailure.Value | 38 | b_ALM_IO_ModuleInternalFailure.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_IO_ModuleInternalFailure.Enable | 39 | b_ALM_IO_ModuleInternalFailure.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_IO_ModuleInternalFailure.AutoReset | 40 | b_ALM_IO_ModuleInternalFailure.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_IO_ModuleInternalFailure.Count | 28 | b_ALM_IO_ModuleInternalFailure.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_IO_PointFailure |  | b_ALM_IO_PointFailure | An IO module has an internal failure. Replace the faulty IO module. Inspect machine for root cause of IO module failure.
| TRUE | ALARMS | b_ALM_IO_PointFailure.Value | 38 | b_ALM_IO_PointFailure.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_IO_PointFailure.Enable | 39 | b_ALM_IO_PointFailure.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_IO_PointFailure.AutoReset | 40 | b_ALM_IO_PointFailure.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_IO_PointFailure.Count | 28 | b_ALM_IO_PointFailure.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PowerSupplyLow |  | b_ALM_PowerSupplyLow | The 24VDC power supply voltage going to the IO modules is low. This 24VDC power is connected to terminals 15 (+) and 16 (-) of module #1 ("X20BR7300"). Check for voltage and wiring integrity.
| TRUE | ALARMS | b_ALM_PowerSupplyLow.Value | 38 | b_ALM_PowerSupplyLow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PowerSupplyLow.Enable | 39 | b_ALM_PowerSupplyLow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PowerSupplyLow.AutoReset | 40 | b_ALM_PowerSupplyLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PowerSupplyLow.Count | 28 | b_ALM_PowerSupplyLow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_LogicSupplyLow |  | b_ALM_LogicSupplyLow | The logic power supply for the IO modules is low. The logic supply is generated by the leftmost module #1 ("X20BR7300"). Check connections between all IO modules & 24VDC. Replace module #1 ("X20BR7300").
| TRUE | ALARMS | b_ALM_LogicSupplyLow.Value | 38 | b_ALM_LogicSupplyLow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_LogicSupplyLow.Enable | 39 | b_ALM_LogicSupplyLow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_LogicSupplyLow.AutoReset | 40 | b_ALM_LogicSupplyLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_LogicSupplyLow.Count | 28 | b_ALM_LogicSupplyLow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_Overtemperature |  | b_ALM_Overtemperature | DISCONNECT POWER TO THE MACHINE! A hardware overtemperature condition has been detected by a missing digital input which is normally energized. This input is typically jumpered to +24VDC, but may be connected through internal optional components (SSRs) or external components at the installation. Check for missing jumper or external equipment. Check for failed cooling fan / blocked airflow on SSRs.
| TRUE | ALARMS | b_ALM_Overtemperature.Value | 38 | b_ALM_Overtemperature.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_Overtemperature.Enable | 39 | b_ALM_Overtemperature.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_Overtemperature.AutoReset | 40 | b_ALM_Overtemperature.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_Overtemperature.Count | 28 | b_ALM_Overtemperature.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_HeaterContactorStuckClosed |  | b_ALM_HeaterContactorStuckClosed | DISCONNECT POWER TO THE MACHINE! The heater contactor has been detected as stuck closed (energized). Cooling water is being introduced and circulated intentionally to cool the heater. The heater contactor has likely welded closed due to overuse or end-of-life. Replace the faulty heater contactor. Check wiring on heater contactor coil & aux contacts.
| TRUE | ALARMS | b_ALM_HeaterContactorStuckClosed.Value | 38 | b_ALM_HeaterContactorStuckClosed.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_HeaterContactorStuckClosed.Enable | 39 | b_ALM_HeaterContactorStuckClosed.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_HeaterContactorStuckClosed.AutoReset | 40 | b_ALM_HeaterContactorStuckClosed.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_HeaterContactorStuckClosed.Count | 28 | b_ALM_HeaterContactorStuckClosed.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_FactoryTempHigh |  | b_ALM_FactoryTemperatureHigh | DISCONNECT POWER TO THE MACHINE! The process loop has exceeded the maximum permitted temperature. Cooling water is being introduced and circulated intentionally to cool the loop. This could be caused by an internal malfunction or oversized external heat source. Replace faulty cooling valve or cooling water supply. Replace faulty heater contactor.
| TRUE | ALARMS | b_ALM_FactoryTempHigh.Value | 38 | b_ALM_FactoryTemperatureHigh.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_FactoryTempHigh.Enable | 39 | b_ALM_FactoryTemperatureHigh.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_FactoryTempHigh.AutoReset | 40 | b_ALM_FactoryTemperatureHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_FactoryTempHigh.Count | 28 | b_ALM_FactoryTemperatureHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_Unbranded |  | b_ALM_Unbranded | No branding nor model has been specified. Set these in "Machine Configuration" within the "Configuration" menu. Select a brand and model for this machine.
| TRUE | ALARMS | b_ALM_Unbranded.Value | 38 | b_ALM_Unbranded.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_Unbranded.Enable | 39 | b_ALM_Unbranded.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_Unbranded.AutoReset | 40 | b_ALM_Unbranded.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_Unbranded.Count | 28 | b_ALM_Unbranded.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_OptionsNotSet |  | b_ALM_OptionsNotSet | The mechanical configuration and factory-installed options have not yet been set. Set these in "Machine Configuration" within the "Configuration" menu. Set the mechanical configuration (pump, heater, etc). Set options (pressure transducers, mold purge, etc).
| TRUE | ALARMS | b_ALM_OptionsNotSet.Value | 38 | b_ALM_OptionsNotSet.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_OptionsNotSet.Enable | 39 | b_ALM_OptionsNotSet.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_OptionsNotSet.AutoReset | 40 | b_ALM_OptionsNotSet.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_OptionsNotSet.Count | 28 | b_ALM_OptionsNotSet.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PhaseMonitor |  | b_ALM_PhaseMonitor | There is a problem with the incoming 3-phase electrical power. This is likely due to reverse phase rotation, a missing phase, or a low leg. For reverse phase rotation, swap any two phases on the incoming power. (This is hazardous work and must be performed by a qualitied electrician). Correct reverse phase rotation or missing phase. Replace blown pump fuse (if equipped).
| TRUE | ALARMS | b_ALM_PhaseMonitor.Value | 38 | b_ALM_PhaseMonitor.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PhaseMonitor.Enable | 39 | b_ALM_PhaseMonitor.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PhaseMonitor.AutoReset | 40 | b_ALM_PhaseMonitor.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PhaseMonitor.Count | 28 | b_ALM_PhaseMonitor.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PumpContactorStuckClosed |  | b_ALM_PumpContactorStuckClosed | DISCONNECT POWER TO THE MACHINE! The pump contactor has been detected as stuck closed (energized). The pump contactor has likely welded closed due to overuse or end-of-life. Replace the faulty pump contactor. Check wiring on pump contactor coil & aux contacts.
| TRUE | ALARMS | b_ALM_PumpContactorStuckClosed.Value | 38 | b_ALM_PumpContactorStuckClosed.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PumpContactorStuckClosed.Enable | 39 | b_ALM_PumpContactorStuckClosed.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PumpContactorStuckClosed.AutoReset | 40 | b_ALM_PumpContactorStuckClosed.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PumpContactorStuckClosed.Count | 28 | b_ALM_PumpContactorStuckClosed.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_HeaterContactorStuckOpen |  | b_ALM_HeaterContactorStuckOpen | The heater contactor has been detected as stuck open (deenergized). The heater contactor likely has a faulty/open coil circuit, or there is mechanical binding on its internal armature which is preventing movement. Replace the faulty heater contactor. Check wiring on heater contactor coil & aux contacts.
| TRUE | ALARMS | b_ALM_HeaterContactorStuckOpen.Value | 38 | b_ALM_HeaterContactorStuckOpen.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_HeaterContactorStuckOpen.Enable | 39 | b_ALM_HeaterContactorStuckOpen.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_HeaterContactorStuckOpen.AutoReset | 40 | b_ALM_HeaterContactorStuckOpen.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_HeaterContactorStuckOpen.Count | 28 | b_ALM_HeaterContactorStuckOpen.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PumpContactorStuckOpen |  | b_ALM_PumpContactorStuckOpen | The pump contactor has been detected as stuck open (deenergized). The pump contactor likely has a faulty/open coil circuit, or there is mechanical binding on its internal armature which is preventing movement. Replace the faulty pump contactor. Check wiring on pump contactor coil & aux contacts.
| TRUE | ALARMS | b_ALM_PumpContactorStuckOpen.Value | 38 | b_ALM_PumpContactorStuckOpen.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PumpContactorStuckOpen.Enable | 39 | b_ALM_PumpContactorStuckOpen.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PumpContactorStuckOpen.AutoReset | 40 | b_ALM_PumpContactorStuckOpen.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PumpContactorStuckOpen.Count | 28 | b_ALM_PumpContactorStuckOpen.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PressureTooHigh |  | b_ALM_PressureTooHigh | Excessive pressure has been detected in the process loop. The source of this pressure is likely from the cooling water supply. This condition can also be caused by a check valve installed on the cooling water inlet without pressure transducers to automatically relieve thermally-induced pressure. Reduce cooling water pressure. Check for stuck closed cooling valve.
| TRUE | ALARMS | b_ALM_PressureTooHigh.Value | 38 | b_ALM_PressureTooHigh.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PressureTooHigh.Enable | 39 | b_ALM_PressureTooHigh.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PressureTooHigh.AutoReset | 40 | b_ALM_PressureTooHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PressureTooHigh.Count | 28 | b_ALM_PressureTooHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_ElecPanelTooHot |  | b_ALM_ElectricPanelTooHot | Excessive temperature has been detected in the electrical panel. This will lead to component failure or erratic operation. The temperature is sensed within the touchscreen controller. Replace the failed electrical panel cooling fan. Check for hot ambient or blocked intake/exhaust vents.
| TRUE | ALARMS | b_ALM_ElecPanelTooHot.Value | 38 | b_ALM_ElectricPanelTooHot.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_ElecPanelTooHot.Enable | 39 | b_ALM_ElectricPanelTooHot.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_ElecPanelTooHot.AutoReset | 40 | b_ALM_ElectricPanelTooHot.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_ElecPanelTooHot.Count | 28 | b_ALM_ElectricPanelTooHot.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_FactoryTempLow |  | b_ALM_FactoryTemperatureLow | The process loop has dropped below the minimum permitted temperature. This could be caused by a low ambient temperature, excessive cooling, or oversized external cooling load. In rare cases, it could also be caused by a malfunctioning RTD temperature sensor. Check for excessively low ambient or large cooling load. Repair stuck-open cooling valve and/or faulty heater.
| TRUE | ALARMS | b_ALM_FactoryTempLow.Value | 38 | b_ALM_FactoryTemperatureLow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_FactoryTempLow.Enable | 39 | b_ALM_FactoryTemperatureLow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_FactoryTempLow.AutoReset | 40 | b_ALM_FactoryTemperatureLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_FactoryTempLow.Count | 28 | b_ALM_FactoryTemperatureLow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_Brownout |  | b_ALM_Brownout | The machine lost incoming power while it was in operation. This alarm was triggered because the machine was configured to do so. To change this behavior, adjust the "Brownout Monitor" settings in "Setup" within the "Configuration" menu. Establish reliable electric power while in operation. Disable fault in "Machine Configuration" if undesired.
| TRUE | ALARMS | b_ALM_Brownout.Value | 38 | b_ALM_Brownout.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_Brownout.Enable | 39 | b_ALM_Brownout.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_Brownout.AutoReset | 40 | b_ALM_Brownout.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_Brownout.Count | 28 | b_ALM_Brownout.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_UserTempHigh |  | b_ALM_UserTemperatureHigh | The process loop has exceeded the maximum limit alarm as configured by the operator. This could be caused by loss of cooling water or excessive external heat load. It could also be an incorrectly configured limit alarm. Check for loss of cooling water or faulty cooling valve. Revise the alarm setting to be more appropriate.
| TRUE | ALARMS | b_ALM_UserTempHigh.Value | 38 | b_ALM_UserTemperatureHigh.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_UserTempHigh.Enable | 39 | b_ALM_UserTemperatureHigh.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_UserTempHigh.AutoReset | 40 | b_ALM_UserTemperatureHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_UserTempHigh.Count | 28 | b_ALM_UserTemperatureHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_UserTempLow |  | b_ALM_UserTemperatureLow | The process loop has dropped below the minimum limit alarm as configured by the operator. This could be caused by excessive cooling water or excessive external cooling load. It could also be an incorrectly configured limit alarm. Check for malfunctioning heater or excessive cool load. Revise the alarm setting to be more appropriate.
| TRUE | ALARMS | b_ALM_UserTempLow.Value | 38 | b_ALM_UserTemperatureLow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_UserTempLow.Enable | 39 | b_ALM_UserTemperatureLow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_UserTempLow.AutoReset | 40 | b_ALM_UserTemperatureLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_UserTempLow.Count | 28 | b_ALM_UserTemperatureLow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PressureBelowMinimum |  | b_ALM_PressureBelowMinimum | Process fluid pressurization supply is too low or there is a leak in the process loop. The machine has been configured to NOT restart automatically if low pressure. To change this, select different actions for "Adaptive Max Setpoint" in "Setup" within the "Configuration" menu.
| TRUE | ALARMS | b_ALM_PressureBelowMinimum.Value | 38 | b_ALM_PressureBelowMinimum.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PressureBelowMinimum.Enable | 39 | b_ALM_PressureBelowMinimum.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PressureBelowMinimum.AutoReset | 40 | b_ALM_PressureBelowMinimum.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PressureBelowMinimum.Count | 28 | b_ALM_PressureBelowMinimum.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PressureNotHighEnough |  | b_ALM_PressureNotHighEnough | Process loop pressure is too low for the actual high system temperature. The process loop is pressurized by the incoming cooling water, and must remain sufficient, especially at high operating temperatures. Increase the cooling water supply pressure. Operate the system at a lower temperature setpoint.
| TRUE | ALARMS | b_ALM_PressureNotHighEnough.Value | 38 | b_ALM_PressureNotHighEnough.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PressureNotHighEnough.Enable | 39 | b_ALM_PressureNotHighEnough.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PressureNotHighEnough.AutoReset | 40 | b_ALM_PressureNotHighEnough.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PressureNotHighEnough.Count | 28 | b_ALM_PressureNotHighEnough.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_LowPressureStandbyTimeout |  | b_ALM_LowPressureStandbyTimeout | Low pressure has been present at the "From Process" port for an excessive amount of time, causing the machine to stop and not execute an automatic restart. There is likely a fault in the external plumbing, such as low pressure or a closed valve.
| TRUE | ALARMS | b_ALM_LowPressureStandbyTimeout.Value | 38 | b_ALM_LowPressureStandbyTimeout.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_LowPressureStandbyTimeout.Enable | 39 | b_ALM_LowPressureStandbyTimeout.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_LowPressureStandbyTimeout.AutoReset | 40 | b_ALM_LowPressureStandbyTimeout.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_LowPressureStandbyTimeout.Count | 28 | b_ALM_LowPressureStandbyTimeout.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_LowPressureStrikeout |  | b_ALM_LowPressureStrikeout | There have been to many low pressure events within a short amount of time. The cooling water plumbing to the equipment is likely too small and is unable to maintain sufficient pressure during operations, or other equipment is consuming too much flow simultaneously. The plumbing to the machine is likely insufficient. Check city/tower/pressure supply or for a leak.
| TRUE | ALARMS | b_ALM_LowPressureStrikeout.Value | 38 | b_ALM_LowPressureStrikeout.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_LowPressureStrikeout.Enable | 39 | b_ALM_LowPressureStrikeout.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_LowPressureStrikeout.AutoReset | 40 | b_ALM_LowPressureStrikeout.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_LowPressureStrikeout.Count | 28 | b_ALM_LowPressureStrikeout.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_PumpOverload |  | b_ALM_PumpOverload | The pump overload protector has tripped from too much pump motor current. This is typically caused by excessive flow in the process loop. Check the fluid loop for too much flow or restrict it. Manually reset overload protector in electrical panel.
| TRUE | ALARMS | b_ALM_PumpOverload.Value | 38 | b_ALM_PumpOverload.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_PumpOverload.Enable | 39 | b_ALM_PumpOverload.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_PumpOverload.AutoReset | 40 | b_ALM_PumpOverload.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_PumpOverload.Count | 28 | b_ALM_PumpOverload.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_FlowmeterLowFlow |  | b_ALM_FlowmeterLowFlow | There is insufficient flow in the process loop for an extended period of time.
| TRUE | ALARMS | b_ALM_FlowmeterLowFlow.Value | 38 | b_ALM_FlowmeterLowFlow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_FlowmeterLowFlow.Enable | 39 | b_ALM_FlowmeterLowFlow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_FlowmeterLowFlow.AutoReset | 40 | b_ALM_FlowmeterLowFlow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_FlowmeterLowFlow.Count | 28 | b_ALM_FlowmeterLowFlow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_SupplyRTD_Open |  | b_ALM_SupplyRTD_Open | An OPEN CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the "To Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "To process" RTD circuit.
| TRUE | ALARMS | b_ALM_SupplyRTD_Open.Value | 38 | b_ALM_SupplyRTD_Open.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_SupplyRTD_Open.Enable | 39 | b_ALM_SupplyRTD_Open.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_SupplyRTD_Open.AutoReset | 40 | b_ALM_SupplyRTD_Open.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_SupplyRTD_Open.Count | 28 | b_ALM_SupplyRTD_Open.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_SupplyRTD_Shorted |  | b_ALM_SupplyRTD_Shorted | A SHORT CIRCUIT has occurred in the "To Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check "To Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "To process" RTD circuit.
| TRUE | ALARMS | b_ALM_SupplyRTD_Shorted.Value | 38 | b_ALM_SupplyRTD_Shorted.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_SupplyRTD_Shorted.Enable | 39 | b_ALM_SupplyRTD_Shorted.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_SupplyRTD_Shorted.AutoReset | 40 | b_ALM_SupplyRTD_Shorted.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_SupplyRTD_Shorted.Count | 28 | b_ALM_SupplyRTD_Shorted.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_SupplyRTD_Other |  | b_ALM_SupplyRTD_Other | A CHANNEL FAULT has occurred in the "To Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit.
| TRUE | ALARMS | b_ALM_SupplyRTD_Other.Value | 38 | b_ALM_SupplyRTD_Other.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_SupplyRTD_Other.Enable | 39 | b_ALM_SupplyRTD_Other.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_SupplyRTD_Other.AutoReset | 40 | b_ALM_SupplyRTD_Other.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_SupplyRTD_Other.Count | 28 | b_ALM_SupplyRTD_Other.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_ReturnRTD_Open |  | b_ALM_ReturnRTD_Open | An OPEN CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check "From Process" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "From process" RTD circuit.
| TRUE | ALARMS | b_ALM_ReturnRTD_Open.Value | 38 | b_ALM_ReturnRTD_Open.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_ReturnRTD_Open.Enable | 39 | b_ALM_ReturnRTD_Open.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_ReturnRTD_Open.AutoReset | 40 | b_ALM_ReturnRTD_Open.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_ReturnRTD_Open.Count | 28 | b_ALM_ReturnRTD_Open.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_ReturnRTD_Shorted |  | b_ALM_ReturnRTD_Shorted | A SHORT CIRCUIT has occurred in the "From Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check "From Process" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "From process" RTD circuit.
| TRUE | ALARMS | b_ALM_ReturnRTD_Shorted.Value | 38 | b_ALM_ReturnRTD_Shorted.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_ReturnRTD_Shorted.Enable | 39 | b_ALM_ReturnRTD_Shorted.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_ReturnRTD_Shorted.AutoReset | 40 | b_ALM_ReturnRTD_Shorted.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_ReturnRTD_Shorted.Count | 28 | b_ALM_ReturnRTD_Shorted.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_ReturnRTD_Other |  | b_ALM_ReturnRTD_Other | A CHANNEL FAULT has occurred in the "From Process" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit.
| TRUE | ALARMS | b_ALM_ReturnRTD_Other.Value | 38 | b_ALM_ReturnRTD_Other.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_ReturnRTD_Other.Enable | 39 | b_ALM_ReturnRTD_Other.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_ReturnRTD_Other.AutoReset | 40 | b_ALM_ReturnRTD_Other.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_ReturnRTD_Other.Count | 28 | b_ALM_ReturnRTD_Other.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_RemoteRTD_Open |  | b_ALM_RemoteRTD_Open | An OPEN CIRCUIT has occurred in the "Remote" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the "Remote" RTD probe for an OPEN CIRCUIT. Check for broken wiring in "Remote" RTD circuit.
| TRUE | ALARMS | b_ALM_RemoteRTD_Open.Value | 38 | b_ALM_RemoteRTD_Open.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_RemoteRTD_Open.Enable | 39 | b_ALM_RemoteRTD_Open.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_RemoteRTD_Open.AutoReset | 40 | b_ALM_RemoteRTD_Open.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_RemoteRTD_Open.Count | 28 | b_ALM_RemoteRTD_Open.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_RemoteRTD_Shorted |  | b_ALM_RemoteRTD_Shorted | A SHORT CIRCUIT has occurred in the "Remote" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the "Remote" RTD probe for a SHORT CIRCUIT. Check for shorted wiring in "Remote" RTD circuit.
| TRUE | ALARMS | b_ALM_RemoteRTD_Shorted.Value | 38 | b_ALM_RemoteRTD_Shorted.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_RemoteRTD_Shorted.Enable | 39 | b_ALM_RemoteRTD_Shorted.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_RemoteRTD_Shorted.AutoReset | 40 | b_ALM_RemoteRTD_Shorted.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_RemoteRTD_Shorted.Count | 28 | b_ALM_RemoteRTD_Shorted.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_RemoteRTD_Other |  | b_ALM_RemoteRTD_Other | A CHANNEL FAULT has occurred in the "Remote" RTD temperature probe or wiring. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check for a malfunctioning RTD input card. Check for extraneous voltages on the RTD circuit.
| TRUE | ALARMS | b_ALM_RemoteRTD_Other.Value | 38 | b_ALM_RemoteRTD_Other.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_RemoteRTD_Other.Enable | 39 | b_ALM_RemoteRTD_Other.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_RemoteRTD_Other.AutoReset | 40 | b_ALM_RemoteRTD_Other.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_RemoteRTD_Other.Count | 28 | b_ALM_RemoteRTD_Other.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_ReturnTransducerHigh |  | b_ALM_ReturnPressureTransducerHigh | A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "From Process" pressure transducer or wiring. This sensor is required for machine operation. Check the "From Process" pressure transducer. Check the analog transducer wiring.
| TRUE | ALARMS | b_ALM_ReturnTransducerHigh.Value | 38 | b_ALM_ReturnPressureTransducerHigh.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_ReturnTransducerHigh.Enable | 39 | b_ALM_ReturnPressureTransducerHigh.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_ReturnTransducerHigh.AutoReset | 40 | b_ALM_ReturnPressureTransducerHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_ReturnTransducerHigh.Count | 28 | b_ALM_ReturnPressureTransducerHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_ReturnTransducerLow |  | b_ALM_ReturnPressureTransducerLow | A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "From Process" pressure transducer or wiring. This sensor is required for machine operation. Check the "From Process" pressure transducer. Check the analog transducer wiring.
| TRUE | ALARMS | b_ALM_ReturnTransducerLow.Value | 38 | b_ALM_ReturnPressureTransducerLow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_ReturnTransducerLow.Enable | 39 | b_ALM_ReturnPressureTransducerLow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_ReturnTransducerLow.AutoReset | 40 | b_ALM_ReturnPressureTransducerLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_ReturnTransducerLow.Count | 28 | b_ALM_ReturnPressureTransducerLow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_ReturnTransducerOther |  | b_ALM_ReturnPressureTransducerOther | A CHANNEL FAULT has occurred on the "From Process" pressure transducer or wiring. This sensor is required for machine operation. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit.
| TRUE | ALARMS | b_ALM_ReturnTransducerOther.Value | 38 | b_ALM_ReturnPressureTransducerOther.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_ReturnTransducerOther.Enable | 39 | b_ALM_ReturnPressureTransducerOther.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_ReturnTransducerOther.AutoReset | 40 | b_ALM_ReturnPressureTransducerOther.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_ReturnTransducerOther.Count | 28 | b_ALM_ReturnPressureTransducerOther.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_SupplyTransducerHigh |  | b_ALM_SupplyPressureTransducerHigh | A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. Check the "To Process" pressure transducer. Check the analog transducer wiring.
| TRUE | ALARMS | b_ALM_SupplyTransducerHigh.Value | 38 | b_ALM_SupplyPressureTransducerHigh.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_SupplyTransducerHigh.Enable | 39 | b_ALM_SupplyPressureTransducerHigh.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_SupplyTransducerHigh.AutoReset | 40 | b_ALM_SupplyPressureTransducerHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_SupplyTransducerHigh.Count | 28 | b_ALM_SupplyPressureTransducerHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_SupplyTransducerLow |  | b_ALM_SupplyPressureTransducerLow | A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the "To Process" pressure transducer or wiring. Check the "To Process" pressure transducer. Check the analog transducer wiring.
| TRUE | ALARMS | b_ALM_SupplyTransducerLow.Value | 38 | b_ALM_SupplyPressureTransducerLow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_SupplyTransducerLow.Enable | 39 | b_ALM_SupplyPressureTransducerLow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_SupplyTransducerLow.AutoReset | 40 | b_ALM_SupplyPressureTransducerLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_SupplyTransducerLow.Count | 28 | b_ALM_SupplyPressureTransducerLow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_SupplyTransducerOther |  | b_ALM_SupplyPressureTransducerOther | A CHANNEL FAULT has occurred on the "To Process" pressure transducer or wiring. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit.
| TRUE | ALARMS | b_ALM_SupplyTransducerOther.Value | 38 | b_ALM_SupplyPressureTransducerOther.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_SupplyTransducerOther.Enable | 39 | b_ALM_SupplyPressureTransducerOther.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_SupplyTransducerOther.AutoReset | 40 | b_ALM_SupplyPressureTransducerOther.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_SupplyTransducerOther.Count | 28 | b_ALM_SupplyPressureTransducerOther.Count | Number of times .Value has been triggered. | Events
| FALSE | ALARMS | b_ALM_AnaProcInHigh |  | b_ALM_AnalogProcessInputHigh | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInHigh.Value | 38 | b_ALM_AnalogProcessInputHigh.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInHigh.Enable | 39 | b_ALM_AnalogProcessInputHigh.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInHigh.AutoReset | 40 | b_ALM_AnalogProcessInputHigh.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInHigh.Count | 28 | b_ALM_AnalogProcessInputHigh.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInLow |  | b_ALM_AnalogProcessInputLow | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInLow.Value | 38 | b_ALM_AnalogProcessInputLow.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInLow.Enable | 39 | b_ALM_AnalogProcessInputLow.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInLow.AutoReset | 40 | b_ALM_AnalogProcessInputLow.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInLow.Count | 28 | b_ALM_AnalogProcessInputLow.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInOther |  | b_ALM_AnalogProcessInputOther | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInOther.Value | 38 | b_ALM_AnalogProcessInputOther.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInOther.Enable | 39 | b_ALM_AnalogProcessInputOther.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInOther.AutoReset | 40 | b_ALM_AnalogProcessInputOther.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaProcInOther.Count | 28 | b_ALM_AnalogProcessInputOther.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcHigh |  | b_ALM_NetworkProcessHigh | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcHigh.Value | 38 | b_ALM_NetworkProcessHigh.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcHigh.Enable | 39 | b_ALM_NetworkProcessHigh.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcHigh.AutoReset | 40 | b_ALM_NetworkProcessHigh.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcHigh.Count | 28 | b_ALM_NetworkProcessHigh.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcLow |  | b_ALM_NetworkProcessLow | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcLow.Value | 38 | b_ALM_NetworkProcessLow.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcLow.Enable | 39 | b_ALM_NetworkProcessLow.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcLow.AutoReset | 40 | b_ALM_NetworkProcessLow.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetProcLow.Count | 28 | b_ALM_NetworkProcessLow.Count | Not currently enabled. | Events | Not currently enabled.
| TRUE | ALARMS | b_ALM_NetProcHeartbeat |  | b_ALM_NetworkProcessHeartbeat | The NETWORK HEARTBEAT HAS BEEN LOST. Heartbeat is necessary because the PROCESS TEMPERATURE is received from the network. To utilize a different process sensor until it can be repaired, select a different "Process Value Source" in "Setup" within the "Configuration" menu. Check the network integrity. Check network settings in originating network node.
| TRUE | ALARMS | b_ALM_NetProcHeartbeat.Value | 38 | b_ALM_NetworkProcessHeartbeat.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_NetProcHeartbeat.Enable | 39 | b_ALM_NetworkProcessHeartbeat.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_NetProcHeartbeat.AutoReset | 40 | b_ALM_NetworkProcessHeartbeat.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_NetProcHeartbeat.Count | 28 | b_ALM_NetworkProcessHeartbeat.Count | Number of times .Value has been triggered. | Events
| FALSE | ALARMS | b_ALM_AnaSP_High |  | b_ALM_AnalogSetpoint_High | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_High.Value | 38 | b_ALM_AnalogSetpoint_High.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_High.Enable | 39 | b_ALM_AnalogSetpoint_High.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_High.AutoReset | 40 | b_ALM_AnalogSetpoint_High.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_High.Count | 28 | b_ALM_AnalogSetpoint_High.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Low |  | b_ALM_AnalogSetpoint_Low | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Low.Value | 38 | b_ALM_AnalogSetpoint_Low.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Low.Enable | 39 | b_ALM_AnalogSetpoint_Low.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Low.AutoReset | 40 | b_ALM_AnalogSetpoint_Low.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Low.Count | 28 | b_ALM_AnalogSetpoint_Low.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Other |  | b_ALM_AnalogSetpoint_Other | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Other.Value | 38 | b_ALM_AnalogSetpoint_Other.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Other.Enable | 39 | b_ALM_AnalogSetpoint_Other.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Other.AutoReset | 40 | b_ALM_AnalogSetpoint_Other.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_AnaSP_Other.Count | 28 | b_ALM_AnalogSetpoint_Other.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_High |  | b_ALM_NetworkSetpoint_High | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_High.Value | 38 | b_ALM_NetworkSetpoint_High.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_High.Enable | 39 | b_ALM_NetworkSetpoint_High.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_High.AutoReset | 40 | b_ALM_NetworkSetpoint_High.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_High.Count | 28 | b_ALM_NetworkSetpoint_High.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Low |  | b_ALM_NetworkSetpoint_Low | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Low.Value | 38 | b_ALM_NetworkSetpoint_Low.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Low.Enable | 39 | b_ALM_NetworkSetpoint_Low.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Low.AutoReset | 40 | b_ALM_NetworkSetpoint_Low.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Low.Count | 28 | b_ALM_NetworkSetpoint_Low.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Heartbeat |  | b_ALM_NetworkSetpoint_Heartbeat | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Heartbeat.Value | 38 | b_ALM_NetworkSetpoint_Heartbeat.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Heartbeat.Enable | 39 | b_ALM_NetworkSetpoint_Heartbeat.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Heartbeat.AutoReset | 40 | b_ALM_NetworkSetpoint_Heartbeat.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_NetSP_Heartbeat.Count | 28 | b_ALM_NetworkSetpoint_Heartbeat.Count | Not currently enabled. | Events | Not currently enabled.
| TRUE | ALARMS | b_ALM_AnaFlowmeterHigh |  | b_ALM_AnalogFlowmeterHigh | A HIGH SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. To continue machine operation, please disable the flowmeter in "Component Configuration" within the "Configuration" menu. Check the flowmeter. Check the analog wiring.
| TRUE | ALARMS | b_ALM_AnaFlowmeterHigh.Value | 38 | b_ALM_AnalogFlowmeterHigh.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_AnaFlowmeterHigh.Enable | 39 | b_ALM_AnalogFlowmeterHigh.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_AnaFlowmeterHigh.AutoReset | 40 | b_ALM_AnalogFlowmeterHigh.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_AnaFlowmeterHigh.Count | 28 | b_ALM_AnalogFlowmeterHigh.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_AnaFlowmeterLow |  | b_ALM_AnalogFlowmeterLow | A LOW SIGNAL or OPEN/SHORT CIRCUIT has occurred on the FLOWMETER or wiring. To continue machine operation, please disable the flowmeter in "Component Configuration" within the "Configuration" menu. Check the flowmeter. Check the analog wiring.
| TRUE | ALARMS | b_ALM_AnaFlowmeterLow.Value | 38 | b_ALM_AnalogFlowmeterLow.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_AnaFlowmeterLow.Enable | 39 | b_ALM_AnalogFlowmeterLow.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_AnaFlowmeterLow.AutoReset | 40 | b_ALM_AnalogFlowmeterLow.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_AnaFlowmeterLow.Count | 28 | b_ALM_AnalogFlowmeterLow.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_AnaFlowmeterOther |  | b_ALM_AnalogFlowmeterOther | A CHANNEL FAULT has occurred on the FLOWMETER or wiring. To continue machine operation, please disable the flowmeter in "Component Configuration" within the "Configuration" menu. Check for a malfunctioning analog input card. Check for extraneous voltages on the analog circuit.
| TRUE | ALARMS | b_ALM_AnaFlowmeterOther.Value | 38 | b_ALM_AnalogFlowmeterOther.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_AnaFlowmeterOther.Enable | 39 | b_ALM_AnalogFlowmeterOther.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_AnaFlowmeterOther.AutoReset | 40 | b_ALM_AnalogFlowmeterOther.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_AnaFlowmeterOther.Count | 28 | b_ALM_AnalogFlowmeterOther.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_HighDeviation |  | b_ALM_HighDeviation | The temperature has deviated too high for too long above the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/blocked cooling valve. Check for a failed (stuck on) heater contactor.
| TRUE | ALARMS | b_ALM_HighDeviation.Value | 38 | b_ALM_HighDeviation.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_HighDeviation.Enable | 39 | b_ALM_HighDeviation.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_HighDeviation.AutoReset | 40 | b_ALM_HighDeviation.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_HighDeviation.Count | 28 | b_ALM_HighDeviation.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_LowDeviation |  | b_ALM_LowDeviation | The temperature has deviated too low for too long below the setpoint. This can be caused by a machine malfunction, or an undersized machine connected to an excessive load. Check for a failed/stuck open cooling valve. Check for a failed heater contactor.
| TRUE | ALARMS | b_ALM_LowDeviation.Value | 38 | b_ALM_LowDeviation.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_LowDeviation.Enable | 39 | b_ALM_LowDeviation.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_LowDeviation.AutoReset | 40 | b_ALM_LowDeviation.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_LowDeviation.Count | 28 | b_ALM_LowDeviation.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_NetworkHeartbeatLost |  | b_ALM_NetworkHeartbeatLost | The NETWORK HEARTBEAT HAS BEEN LOST after having been initially established. Fix network or remote node. Change Network Timeout action or timeout period.
| TRUE | ALARMS | b_ALM_NetworkHeartbeatLost.Value | 38 | b_ALM_NetworkHeartbeatLost.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_NetworkHeartbeatLost.Enable | 39 | b_ALM_NetworkHeartbeatLost.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_NetworkHeartbeatLost.AutoReset | 40 | b_ALM_NetworkHeartbeatLost.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_NetworkHeartbeatLost.Count | 28 | b_ALM_NetworkHeartbeatLost.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_RemoteSlaveAlarmActive |  | b_ALM_RemoteSlaveAlarmActive | An alarm has been inherrited from banked Slave unit. Rectify the alarm on the banked slave unit. Change the master to not register banked slave alarms.
| TRUE | ALARMS | b_ALM_RemoteSlaveAlarmActive.Value | 38 | b_ALM_RemoteSlaveAlarmActive.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_RemoteSlaveAlarmActive.Enable | 39 | b_ALM_RemoteSlaveAlarmActive.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_RemoteSlaveAlarmActive.AutoReset | 40 | b_ALM_RemoteSlaveAlarmActive.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_RemoteSlaveAlarmActive.Count | 28 | b_ALM_RemoteSlaveAlarmActive.Count | Number of times .Value has been triggered. | Events
| TRUE | ALARMS | b_ALM_RampSoakPaused |  | b_ALM_RampSoakPaused | The Ramp/Soak sequence was interrupted by a low pressure condition for too long. The machine will not execute an automatic restart since it would disrupt the sensitive Ramp/Soak sequence that it was attempting to execute.
| TRUE | ALARMS | b_ALM_RampSoakPaused.Value | 38 | b_ALM_RampSoakPaused.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active
| TRUE | ALARMS | b_ALM_RampSoakPaused.Enable | 39 | b_ALM_RampSoakPaused.Enable | If enabled, the alam is ready to be triggered once conditions exist. If disabled, .Value will never become active, even if conditions exist to trigger the alarm. | Disabled/Enabled
| TRUE | ALARMS | b_ALM_RampSoakPaused.AutoReset | 40 | b_ALM_RampSoakPaused.AutoReset | Whether or not .Value will automatically reset when triggering conditions no longer exist. If False, the alarm would require a fault reset in order to reset .Value. | Manual/Auto
| TRUE | ALARMS | b_ALM_RampSoakPaused.Count | 28 | b_ALM_RampSoakPaused.Count | Number of times .Value has been triggered. | Events
| FALSE | ALARMS | b_ALM_PID_AT_InitOutputTooHigh |  | b_ALM_PID_Autotune_InitialOutputTooHigh | PID autotune's starting control output is too high. Autotune cannot complete successfully. Existing PID settings will remain untouched. TBD TBD |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_InitOutputTooHigh.Value | 38 | b_ALM_PID_Autotune_InitialOutputTooHigh.Value | This bit signifies whether or not this alarm is currently active. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_InitOutputTooHigh.Enable | 39 | b_ALM_PID_Autotune_InitialOutputTooHigh.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_InitOutputTooHigh.AutoReset | 40 | b_ALM_PID_Autotune_InitialOutputTooHigh.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_InitOutputTooHigh.Count | 28 | b_ALM_PID_Autotune_InitialOutputTooHigh.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcResponseSlow |  | b_ALM_PID_Autotune_ProcessResponseSlow | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcResponseSlow.Value | 38 | b_ALM_PID_Autotune_ProcessResponseSlow.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcResponseSlow.Enable | 39 | b_ALM_PID_Autotune_ProcessResponseSlow.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcResponseSlow.AutoReset | 40 | b_ALM_PID_Autotune_ProcessResponseSlow.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcResponseSlow.Count | 28 | b_ALM_PID_Autotune_ProcessResponseSlow.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_TimeConstNotFound |  | b_ALM_PID_Autotune_TimeConstantNotFound | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_TimeConstNotFound.Value | 38 | b_ALM_PID_Autotune_TimeConstantNotFound.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_TimeConstNotFound.Enable | 39 | b_ALM_PID_Autotune_TimeConstantNotFound.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_TimeConstNotFound.AutoReset | 40 | b_ALM_PID_Autotune_TimeConstantNotFound.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_TimeConstNotFound.Count | 28 | b_ALM_PID_Autotune_TimeConstantNotFound.Count | Not currently enabled. | Events | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcLimitExceeded |  | b_ALM_PID_Autotune_ProcessLimitExceeded | Not currently enabled. |  | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcLimitExceeded.Value | 38 | b_ALM_PID_Autotune_ProcessLimitExceeded.Value | Not currently enabled. | Inactive/Active | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcLimitExceeded.Enable | 39 | b_ALM_PID_Autotune_ProcessLimitExceeded.Enable | Not currently enabled. | Disabled/Enabled | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcLimitExceeded.AutoReset | 40 | b_ALM_PID_Autotune_ProcessLimitExceeded.AutoReset | Not currently enabled. | Manual/Auto | Not currently enabled.
| FALSE | ALARMS | b_ALM_PID_AT_ProcLimitExceeded.Count | 28 | b_ALM_PID_Autotune_ProcessLimitExceeded.Count | Not currently enabled. | Events | Not currently enabled.
Hardware Digital Inputs
| TRUE | INPUTS_DIG | b_IN_PressureSwitch |  | b_IN_PressureSwitch | Status of pressure switch on return (from process) side of process loop. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PressureSwitch.Value | 41 | b_IN_PressureSwitch.Value | Status of pressure switch on return (from process) side of process loop. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PressureSwitch.Implemented | 41 | b_IN_PressureSwitch.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_PressureSwitch.Error |  | b_IN_PressureSwitch.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_PumpContactorAux |  | b_IN_PumpContactorAux | Status of the pump contactor, as indicated by a set of auxiliary contacts on the contactor. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PumpContactorAux.Value | 41 | b_IN_PumpContactorAux.Value | Status of the pump contactor, as indicated by a set of auxiliary contacts on the contactor. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PumpContactorAux.Implemented | 41 | b_IN_PumpContactorAux.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_PumpContactorAux.Error |  | b_IN_PumpContactorAux.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_PumpOverload |  | b_IN_PumpOverload | Status of pump overload. No overload = TRUE; Tripped overload = FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PumpOverload.Value | 41 | b_IN_PumpOverload.Value | Status of pump overload. No overload = TRUE; Tripped overload = FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PumpOverload.Implemented | 41 | b_IN_PumpOverload.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_PumpOverload.Error |  | b_IN_PumpOverload.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_HeaterContactorAux |  | b_IN_HeaterContactorAux | Status of the pump contactor, as indicated by a set of auxiliary contacts on the contactor. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_HeaterContactorAux.Value | 41 | b_IN_HeaterContactorAux.Value | Status of the pump contactor, as indicated by a set of auxiliary contacts on the contactor. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_HeaterContactorAux.Implemented | 41 | b_IN_HeaterContactorAux.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_HeaterContactorAux.Error |  | b_IN_HeaterContactorAux.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_PhaseMonitor |  | b_IN_PhaseMonitor | Status of phase monitor. Phases OK=TRUE; Phase Error=FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PhaseMonitor.Value | 41 | b_IN_PhaseMonitor.Value | Status of phase monitor. Phases OK=TRUE; Phase Error=FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_PhaseMonitor.Implemented | 41 | b_IN_PhaseMonitor.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_PhaseMonitor.Error |  | b_IN_PhaseMonitor.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_HeaterHighTemp |  | b_IN_HeaterHighTemperature | Status of an external high temperature switch. Temp OK=TRUE; Overtemp=FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_HeaterHighTemp.Value | 41 | b_IN_HeaterHighTemperature.Value | Status of an external high temperature switch. Temp OK=TRUE; Overtemp=FALSE. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_HeaterHighTemp.Implemented | 41 | b_IN_HeaterHighTemperature.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_HeaterHighTemp.Error |  | b_IN_HeaterHighTemperature.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_Flowswitch |  | b_IN_Flowswitch | Status of flowswitch in the process loop. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_Flowswitch.Value | 41 | b_IN_Flowswitch.Value | Status of flowswitch in the process loop. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_Flowswitch.Implemented | 41 | b_IN_Flowswitch.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_Flowswitch.Error |  | b_IN_Flowswitch.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_RemoteStart |  | b_IN_RemoteStart | Status of remote start input. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_RemoteStart.Value | 41 | b_IN_RemoteStart.Value | Status of remote start input. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_RemoteStart.Implemented | 41 | b_IN_RemoteStart.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_RemoteStart.Error |  | b_IN_RemoteStart.Error | 10=No error, 0=Error. | <enumeration>
| TRUE | INPUTS_DIG | b_IN_SetpointSelectAdvance |  | b_IN_SetpointSelectAdvance | Status of Setpoint Select / Ramp/Soak Step Advance input. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_SetpointSelectAdvance.Value | 41 | b_IN_SetpointSelectAdvance.Value | Status of Setpoint Select / Ramp/Soak Step Advance input. TRUE if voltage is high to input. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_DIG | b_IN_SetpointSelectAdvance.Implemented | 41 | b_IN_SetpointSelectAdvance.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_DIG | b_IN_SetpointSelectAdvance.Error |  | b_IN_SetpointSelectAdvance.Error | 10=No error, 0=Error. | <enumeration>
Hardware Analog Inputs
| TRUE | INPUTS_ANA | r_IN_SupplyRTD |  | r_IN_SupplyRTD | Temperature of the Supply (To Process) RTD. No smoothing is applied. In units of °C. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_SupplyRTD.Value | 2 | r_IN_SupplyRTD.Value | Value of Supply (To Process) RTD input. In units of degrees Celsius (°C). Offset according to calibration parameter(s). Only valid if .Implemented is TRUE, and .Error is "10". | °C | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_SupplyRTD.Implemented | 41 | r_IN_SupplyRTD.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_SupplyRTD.Error |  | r_IN_SupplyRTD.Error | 0=Not in use; -2=Probe Short Circuit; -1=Probe not connected; 10=No error | <enumeration>
| TRUE | INPUTS_ANA | r_IN_ReturnRTD |  | r_IN_ReturnRTD | Tempertaure of the Return (From Process) RTD. No smoothing is applied. In units of °C. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_ReturnRTD.Value | 2 | r_IN_ReturnRTD.Value | Value of Return (From Process) RTD input. In units of degrees Celsius (°C). Offset according to calibration parameter(s). Only valid if .Implemented is TRUE, and .Error is "10". | °C | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_ReturnRTD.Implemented | 41 | r_IN_ReturnRTD.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_ReturnRTD.Error |  | r_IN_ReturnRTD.Error | 0=Not in use; -2=Probe Short Circuit; -1=Probe not connected; 10=No error | <enumeration>
| TRUE | INPUTS_ANA | r_IN_RemoteRTD |  | r_IN_RemoteRTD | Tempertaure of the Remote RTD. In units of °C. No smoothing is applied. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_RemoteRTD.Value | 2 | r_IN_RemoteRTD.Value | Value of Remote RTD input. In units of degrees Celsius (°C). Offset according to calibration parameter(s). Only valid if .Implemented is TRUE, and .Error is "10". | °C | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_RemoteRTD.Implemented | 41 | r_IN_RemoteRTD.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_RemoteRTD.Error |  | r_IN_RemoteRTD.Error | 0=Not in use; -2=Probe Short Circuit; -1=Probe not connected; 10=No error | <enumeration>
| TRUE | INPUTS_ANA | r_IN_SupplyPressure |  | r_IN_SupplyPressure | Pressure measured by the Supply (To Process) transducer. No smoothing is applied. In units of psi. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_SupplyPressure.Value | 13 | r_IN_SupplyPressure.Value | Value of Supply (To Process) input. In units of pounds per square inch (psi). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | psi | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_SupplyPressure.Implemented | 41 | r_IN_SupplyPressure.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_SupplyPressure.Error |  | r_IN_SupplyPressure.Error | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Sensor not connected; 10=No error | <enumeration>
| TRUE | INPUTS_ANA | r_IN_ReturnPressure |  | r_IN_ReturnPressure | Pressure measured by the Return (From Process) transducer. No smoothing is applied. In units of psi. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_ReturnPressure.Value | 13 | r_IN_ReturnPressure.Value | Value of Return (From Process) input. In units of pounds per square inch (psi). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | psi | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_ReturnPressure.Implemented | 41 | r_IN_ReturnPressure.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_ReturnPressure.Error |  | r_IN_ReturnPressure.Error | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Sensor not connected; 10=No error | <enumeration>
| FALSE | INPUTS_ANA | r_IN_AnalogSetpoint |  | r_IN_AnalogSetpoint | Setpoint determined by an external analog signal. In units of °C. Not yet implemented. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| FALSE | INPUTS_ANA | r_IN_AnalogSetpoint.Value | 2 | r_IN_AnalogSetpoint.Value | Not currently implemented. | °C | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| FALSE | INPUTS_ANA | r_IN_AnalogSetpoint.Implemented | 41 | r_IN_AnalogSetpoint.Implemented | Not currently implemented. | On/Off
| FALSE | INPUTS_ANA | r_IN_AnalogSetpoint.Error |  | r_IN_AnalogSetpoint.Error | Not currently implemented. | <enumeration>
| TRUE | INPUTS_ANA | r_IN_AnalogFlowmeter |  | r_IN_AnalogFlowmeter | Flow measured by an analog flow meter. In units of gpm. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_AnalogFlowmeter.Value | 5 | r_IN_AnalogFlowmeter.Value | Flow measured by an analog flow meter. In units of gpm. | gpm | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_AnalogFlowmeter.Implemented | 41 | r_IN_AnalogFlowmeter.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_AnalogFlowmeter.Error |  | r_IN_AnalogFlowmeter.Error | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Flowmeter not connected; 10=No error | <enumeration>
| FALSE | INPUTS_ANA | r_IN_AnalogProcess |  | r_IN_AnalogProcess | Tempertaure of an extrernal process temperature signal. In units of °C. Not yet implemented. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| FALSE | INPUTS_ANA | r_IN_AnalogProcess.Value | 2 | r_IN_AnalogProcess.Value | Not currently implemented. | °C | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| FALSE | INPUTS_ANA | r_IN_AnalogProcess.Implemented | 41 | r_IN_AnalogProcess.Implemented | Not currently implemented. | On/Off
| FALSE | INPUTS_ANA | r_IN_AnalogProcess.Error |  | r_IN_AnalogProcess.Error | Not currently implemented. | <enumeration>
| TRUE | INPUTS_ANA | r_IN_RemoteResistorControl |  | r_IN_RemoteResistorControl | Value of remote resistor control input. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_RemoteResistorControl.Value | #N/A | r_IN_RemoteResistorControl.Value | Value of remote resistor control input. In units of ohms (Ω). Only valid if .Implemented is TRUE, and .Error is "10". | ohms | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_RemoteResistorControl.Implemented | 41 | r_IN_RemoteResistorControl.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_RemoteResistorControl.Error |  | r_IN_RemoteResistorControl.Error | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Nothing connected; 10=No error | <enumeration>
| TRUE | INPUTS_ANA | r_IN_ElecEnclosureTemp |  | r_IN_ElectricalEnclosureTemp | Value of enclosure temperature input. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_ElecEnclosureTemp.Value | 2 | r_IN_ElectricalEnclosureTemp.Value | Value of enclosure temperature input. In units of degrees Celsius (°C). Only valid if .Implemented is TRUE, and .Error is "10". | °C | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_ElecEnclosureTemp.Implemented | 41 | r_IN_ElectricalEnclosureTemp.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_ElecEnclosureTemp.Error |  | r_IN_ElectricalEnclosureTemp.Error | 0=Not in use; -4=Value underflow; -3=Value overflow; -1=Sensor not connected; 10=No error | <enumeration>
| TRUE | INPUTS_ANA | r_IN_PulseFlowmeter |  | r_IN_PulseFlowmeter | Flow measured by a pulse flow meter. |  | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_PulseFlowmeter.Value | 5 | r_IN_PulseFlowmeter.Value | Value of pulse flowmeter input in the process loop. In units of gallon per minute (gpm). K-Factor is already applied to this number. Only valid if .Implemented is TRUE, and .Error is "10". | gpm | Value of input. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | INPUTS_ANA | r_IN_PulseFlowmeter.Implemented | 41 | r_IN_PulseFlowmeter.Implemented | This input is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | INPUTS_ANA | r_IN_PulseFlowmeter.Error |  | r_IN_PulseFlowmeter.Error | 0=Not in use; 10=No error | <enumeration>
Hardware Digital Outputs
| TRUE | OUTPUTS_DIG | b_OUT_PumpContactor |  | b_OUT_PumpContactor | Status of pump contactor output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_PumpContactor.Value | 41 | b_OUT_PumpContactor.Value | Status of pump contactor output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_PumpContactor.Implemented | 41 | b_OUT_PumpContactor.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_PumpContactor.Error |  | b_OUT_PumpContactor.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_HeaterContactor |  | b_OUT_HeaterContactor | Status of heater electromechanical contactor output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_HeaterContactor.Value | 41 | b_OUT_HeaterContactor.Value | Status of heater electromechanical contactor output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_HeaterContactor.Implemented | 41 | b_OUT_HeaterContactor.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_HeaterContactor.Error |  | b_OUT_HeaterContactor.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_HeaterSSR |  | b_OUT_HeaterSolidStateRelay | Status of heater SSR output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_HeaterSSR.Value | 41 | b_OUT_HeaterSolidStateRelay.Value | Status of heater SSR output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_HeaterSSR.Implemented | 41 | b_OUT_HeaterSolidStateRelay.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_HeaterSSR.Error |  | b_OUT_HeaterSolidStateRelay.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_CoolingValveOpen |  | b_OUT_CoolingValveOpen | Status of cooling valve (open) output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_CoolingValveOpen.Value | 41 | b_OUT_CoolingValveOpen.Value | Status of cooling valve (open) output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_CoolingValveOpen.Implemented | 41 | b_OUT_CoolingValveOpen.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_CoolingValveOpen.Error |  | b_OUT_CoolingValveOpen.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_MoldPurge |  | b_OUT_MoldPurge | Status of mold purge solenoid valve output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_MoldPurge.Value | 41 | b_OUT_MoldPurge.Value | Status of mold purge solenoid valve output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_MoldPurge.Implemented | 41 | b_OUT_MoldPurge.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_MoldPurge.Error |  | b_OUT_MoldPurge.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_AlarmSilenceable |  | b_OUT_AlarmSilenceable | Status of silenceable alarm output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_AlarmSilenceable.Value | 41 | b_OUT_AlarmSilenceable.Value | Status of silenceable alarm output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_AlarmSilenceable.Implemented | 41 | b_OUT_AlarmSilenceable.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_AlarmSilenceable.Error |  | b_OUT_AlarmSilenceable.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_AlarmNonSilenceable |  | b_OUT_AlarmNonSilenceable | Status of non-silenceable alarm output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_AlarmNonSilenceable.Value | 41 | b_OUT_AlarmNonSilenceable.Value | Status of non-silenceable alarm output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_AlarmNonSilenceable.Implemented | 41 | b_OUT_AlarmNonSilenceable.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_AlarmNonSilenceable.Error |  | b_OUT_AlarmNonSilenceable.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_Vent |  | b_OUT_Vent | Status of vent solenoid output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_Vent.Value | 41 | b_OUT_Vent.Value | Status of vent solenoid output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_Vent.Implemented | 41 | b_OUT_Vent.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_Vent.Error |  | b_OUT_Vent.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
| TRUE | OUTPUTS_DIG | b_OUT_FillValve |  | b_OUT_FillValve | Status of fill solenoid output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". |  | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_FillValve.Value | 41 | b_OUT_FillValve.Value | Status of fill solenoid output. TRUE if voltage from the output is active. Only valid if .Implemented is TRUE, and .Error is "10". | On/Off | Status of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_DIG | b_OUT_FillValve.Implemented | 41 | b_OUT_FillValve.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_DIG | b_OUT_FillValve.Error |  | b_OUT_FillValve.Error | 0=Not in use; 1=Short circuit; 10=No error | <enumeration>
Hardware Analog Outputs
| TRUE | OUTPUTS_ANA | r_OUT_ModulatingCoolingValve |  | r_OUT_ModulatingCoolingValve | Value of analog output for cooling modulating valve. |  | Value of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_ANA | r_OUT_ModulatingCoolingValve.Value | 11 | r_OUT_ModulatingCoolingValve.Value | Value of analog output for cooling modulating valve. In units of percent (%). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | % | Value of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_ANA | r_OUT_ModulatingCoolingValve.Implemented | 41 | r_OUT_ModulatingCoolingValve.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_ANA | r_OUT_ModulatingCoolingValve.Error |  | r_OUT_ModulatingCoolingValve.Error | 0=Not in use; 10=No error | <enumeration>
| TRUE | OUTPUTS_ANA | r_OUT_AnalogProcessRetransmit |  | r_OUT_AnalogProcessRetransmit | Value of analog output for process value retransmit. |  | Value of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_ANA | r_OUT_AnalogProcessRetransmit.Value | 2 | r_OUT_AnalogProcessRetransmit.Value | Value of analog output for process value retransmit. In units of degrees Celsius (°C). Scaled according to analog scaling parameters for this channel. Only valid if .Implemented is TRUE, and .Error is "10". | °C | Value of output. Only valid if .Implemented is TRUE, and .Error is "10".
| TRUE | OUTPUTS_ANA | r_OUT_AnalogProcessRetransmit.Implemented | 41 | r_OUT_AnalogProcessRetransmit.Implemented | This output is only valid on the unit if .Implemented is TRUE. | On/Off
| TRUE | OUTPUTS_ANA | r_OUT_AnalogProcessRetransmit.Error |  | r_OUT_AnalogProcessRetransmit.Error | 0=Not in use; 10=No error | <enumeration>
Ramp/Soak
| TRUE | RAMP_SOAK | n_RampSoakMaxSteps | 30 | n_RampSoakMaxSteps | Maximum number of steps permitted for Ramp/Soak | steps
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.InterimSetpointSts | 2 | st_NET_RampSoakRecipe.InterimSetpointSts | The interim setpoint if the step is time-limited or rate-limited. In units of °C. | °C
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.NextActionCountdown | 8 | st_NET_RampSoakRecipe.NextActionCountdown | Time countdown for the next action in a ramp/soak sequence. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps |  |  | Number of possible steps in the Ramp/Soak.
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1] |  | st_NET_RampSoakRecipe.Steps[1] | Ramp/Soak Step #1 parameters.
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].LimitStartsAtPV | 32 | st_NET_RampSoakRecipe.Steps[1].LimitStartsAtProcessValue | Ramp/Soak Step #1: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step (first step based on process value at unit startup). | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].NextAction |  | st_NET_RampSoakRecipe.Steps[1].NextAction | Ramp/Soak Step #1: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].NextStep |  | st_NET_RampSoakRecipe.Steps[1].NextStep | Ramp/Soak Step #1: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].Setpoint | 2 | st_NET_RampSoakRecipe.Steps[1].Setpoint | Ramp/Soak Step #1: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].StepActive | 32 | st_NET_RampSoakRecipe.Steps[1].StepActive | Ramp/Soak Step #1: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].StepDuration | 8 | st_NET_RampSoakRecipe.Steps[1].StepDuration | Ramp/Soak Step #1: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].TempRateLimit | 25 | st_NET_RampSoakRecipe.Steps[1].TemperatureRateLimit | Ramp/Soak Step #1: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].TimedRateLimit | 8 | st_NET_RampSoakRecipe.Steps[1].TimedRateLimit | Ramp/Soak Step #1: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[1].TriggerForNext |  | st_NET_RampSoakRecipe.Steps[1].TriggerForNext | Ramp/Soak Step #1: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2] |  | st_NET_RampSoakRecipe.Steps[2] | Ramp/Soak Step #2 parameters.
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].LimitStartsAtPV | 32 | st_NET_RampSoakRecipe.Steps[2].LimitStartsAtProcessValue | Ramp/Soak Step #2: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].NextAction |  | st_NET_RampSoakRecipe.Steps[2].NextAction | Ramp/Soak Step #2: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].NextStep |  | st_NET_RampSoakRecipe.Steps[2].NextStep | Ramp/Soak Step #2: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].Setpoint | 2 | st_NET_RampSoakRecipe.Steps[2].Setpoint | Ramp/Soak Step #2: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].StepActive | 32 | st_NET_RampSoakRecipe.Steps[2].StepActive | Ramp/Soak Step #2: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].StepDuration | 8 | st_NET_RampSoakRecipe.Steps[2].StepDuration | Ramp/Soak Step #2: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].TempRateLimit | 25 | st_NET_RampSoakRecipe.Steps[2].TemperatureRateLimit | Ramp/Soak Step #2: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].TimedRateLimit | 8 | st_NET_RampSoakRecipe.Steps[2].TimedRateLimit | Ramp/Soak Step #2: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[2].TriggerForNext |  | st_NET_RampSoakRecipe.Steps[2].TriggerForNext | Ramp/Soak Step #2: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3] |  | st_NET_RampSoakRecipe.Steps[3] | Ramp/Soak Step #3 parameters.
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].LimitStartsAtPV | 32 | st_NET_RampSoakRecipe.Steps[3].LimitStartsAtProcessValue | Ramp/Soak Step #3: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].NextAction |  | st_NET_RampSoakRecipe.Steps[3].NextAction | Ramp/Soak Step #3: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].NextStep |  | st_NET_RampSoakRecipe.Steps[3].NextStep | Ramp/Soak Step #3: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].Setpoint | 2 | st_NET_RampSoakRecipe.Steps[3].Setpoint | Ramp/Soak Step #3: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].StepActive | 32 | st_NET_RampSoakRecipe.Steps[3].StepActive | Ramp/Soak Step #3: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].StepDuration | 8 | st_NET_RampSoakRecipe.Steps[3].StepDuration | Ramp/Soak Step #3: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].TempRateLimit | 25 | st_NET_RampSoakRecipe.Steps[3].TemperatureRateLimit | Ramp/Soak Step #3: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].TimedRateLimit | 8 | st_NET_RampSoakRecipe.Steps[3].TimedRateLimit | Ramp/Soak Step #3: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[3].TriggerForNext |  | st_NET_RampSoakRecipe.Steps[3].TriggerForNext | Ramp/Soak Step #3: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4] |  | st_NET_RampSoakRecipe.Steps[4] | Ramp/Soak Step #4 parameters.
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].LimitStartsAtPV | 32 | st_NET_RampSoakRecipe.Steps[4].LimitStartsAtProcessValue | Ramp/Soak Step #4: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].NextAction |  | st_NET_RampSoakRecipe.Steps[4].NextAction | Ramp/Soak Step #4: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].NextStep |  | st_NET_RampSoakRecipe.Steps[4].NextStep | Ramp/Soak Step #4: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].Setpoint | 2 | st_NET_RampSoakRecipe.Steps[4].Setpoint | Ramp/Soak Step #4: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].StepActive | 32 | st_NET_RampSoakRecipe.Steps[4].StepActive | Ramp/Soak Step #4: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].StepDuration | 8 | st_NET_RampSoakRecipe.Steps[4].StepDuration | Ramp/Soak Step #4: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].TempRateLimit | 25 | st_NET_RampSoakRecipe.Steps[4].TemperatureRateLimit | Ramp/Soak Step #4: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].TimedRateLimit | 8 | st_NET_RampSoakRecipe.Steps[4].TimedRateLimit | Ramp/Soak Step #4: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[4].TriggerForNext |  | st_NET_RampSoakRecipe.Steps[4].TriggerForNext | Ramp/Soak Step #4: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5] |  | st_NET_RampSoakRecipe.Steps[5] | Ramp/Soak Step #5 parameters.
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].LimitStartsAtPV | 32 | st_NET_RampSoakRecipe.Steps[5].LimitStartsAtProcessValue | Ramp/Soak Step #5: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].NextAction |  | st_NET_RampSoakRecipe.Steps[5].NextAction | Ramp/Soak Step #5: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].NextStep |  | st_NET_RampSoakRecipe.Steps[5].NextStep | Ramp/Soak Step #5: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].Setpoint | 2 | st_NET_RampSoakRecipe.Steps[5].Setpoint | Ramp/Soak Step #5: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].StepActive | 32 | st_NET_RampSoakRecipe.Steps[5].StepActive | Ramp/Soak Step #5: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].StepDuration | 8 | st_NET_RampSoakRecipe.Steps[5].StepDuration | Ramp/Soak Step #5: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].TempRateLimit | 25 | st_NET_RampSoakRecipe.Steps[5].TemperatureRateLimit | Ramp/Soak Step #5: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].TimedRateLimit | 8 | st_NET_RampSoakRecipe.Steps[5].TimedRateLimit | Ramp/Soak Step #5: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_NET_RampSoakRecipe.Steps[5].TriggerForNext |  | st_NET_RampSoakRecipe.Steps[5].TriggerForNext | Ramp/Soak Step #5: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | b_RampSoakRecipe_RemWriteAccess | 32 | b_RampSoakRecipe_RemWriteAccess | FALSE=The ramp/soak recipe is currently read-only; TRUE=The ramp/soak recipie can be currently changed via the "To Set" parameters. | No/Yes
| TRUE | RAMP_SOAK | b_RampSoakRecipe_WriteRemoteData | 32 | b_RampSoakRecipe_WriteRemoteData | Set TRUE to load the "To Set" data into the current recipie. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps |  | st_RampSoakRecipeToSet.Steps | Number of possible steps in the Ramp/Soak.
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1] |  | st_RampSoakRecipeToSet.Steps[1] | Ramp/Soak Step #1 parameters.
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].LimitStartsAtPV | 32 | st_RampSoakRecipeToSet.Steps[1].LimitStartsAtProcessValue | Ramp/Soak Step #1 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step (first step based on process value at unit startup). | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].NextAction |  | st_RampSoakRecipeToSet.Steps[1].NextAction | Ramp/Soak Step #1 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].NextStep |  | st_RampSoakRecipeToSet.Steps[1].NextStep | Ramp/Soak Step #1 to set: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].Setpoint | 2 | st_RampSoakRecipeToSet.Steps[1].Setpoint | Ramp/Soak Step #1 to set: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].StepActive | 32 | st_RampSoakRecipeToSet.Steps[1].StepActive | Ramp/Soak Step #1 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].StepDuration | 8 | st_RampSoakRecipeToSet.Steps[1].StepDuration | Ramp/Soak Step #1 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].TempRateLimit | 25 | st_RampSoakRecipeToSet.Steps[1].TemperatureRateLimit | Ramp/Soak Step #1 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].TimedRateLimit | 8 | st_RampSoakRecipeToSet.Steps[1].TimedRateLimit | Ramp/Soak Step #1 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[1].TriggerForNext |  | st_RampSoakRecipeToSet.Steps[1].TriggerForNext | Ramp/Soak Step #1 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2] |  | st_RampSoakRecipeToSet.Steps[2] | Ramp/Soak Step #2 parameters.
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].LimitStartsAtPV | 32 | st_RampSoakRecipeToSet.Steps[2].LimitStartsAtProcessValue | Ramp/Soak Step #2 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].NextAction |  | st_RampSoakRecipeToSet.Steps[2].NextAction | Ramp/Soak Step #2 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].NextStep |  | st_RampSoakRecipeToSet.Steps[2].NextStep | Ramp/Soak Step #2 to set: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].Setpoint | 2 | st_RampSoakRecipeToSet.Steps[2].Setpoint | Ramp/Soak Step #2 to set: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].StepActive | 32 | st_RampSoakRecipeToSet.Steps[2].StepActive | Ramp/Soak Step #2 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].StepDuration | 8 | st_RampSoakRecipeToSet.Steps[2].StepDuration | Ramp/Soak Step #2 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].TempRateLimit | 25 | st_RampSoakRecipeToSet.Steps[2].TemperatureRateLimit | Ramp/Soak Step #2 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].TimedRateLimit | 8 | st_RampSoakRecipeToSet.Steps[2].TimedRateLimit | Ramp/Soak Step #2 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[2].TriggerForNext |  | st_RampSoakRecipeToSet.Steps[2].TriggerForNext | Ramp/Soak Step #2 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3] |  | st_RampSoakRecipeToSet.Steps[3] | Ramp/Soak Step #3 parameters.
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].LimitStartsAtPV | 32 | st_RampSoakRecipeToSet.Steps[3].LimitStartsAtProcessValue | Ramp/Soak Step #3 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].NextAction |  | st_RampSoakRecipeToSet.Steps[3].NextAction | Ramp/Soak Step #3 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].NextStep |  | st_RampSoakRecipeToSet.Steps[3].NextStep | Ramp/Soak Step #3 to set: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].Setpoint | 2 | st_RampSoakRecipeToSet.Steps[3].Setpoint | Ramp/Soak Step #3 to set: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].StepActive | 32 | st_RampSoakRecipeToSet.Steps[3].StepActive | Ramp/Soak Step #3 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].StepDuration | 8 | st_RampSoakRecipeToSet.Steps[3].StepDuration | Ramp/Soak Step #3 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].TempRateLimit | 25 | st_RampSoakRecipeToSet.Steps[3].TemperatureRateLimit | Ramp/Soak Step #3 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].TimedRateLimit | 8 | st_RampSoakRecipeToSet.Steps[3].TimedRateLimit | Ramp/Soak Step #3 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[3].TriggerForNext |  | st_RampSoakRecipeToSet.Steps[3].TriggerForNext | Ramp/Soak Step #3 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4] |  | st_RampSoakRecipeToSet.Steps[4] | Ramp/Soak Step #4 parameters.
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].LimitStartsAtPV | 32 | st_RampSoakRecipeToSet.Steps[4].LimitStartsAtProcessValue | Ramp/Soak Step #4 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].NextAction |  | st_RampSoakRecipeToSet.Steps[4].NextAction | Ramp/Soak Step #4 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].NextStep |  | st_RampSoakRecipeToSet.Steps[4].NextStep | Ramp/Soak Step #4 to set: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].Setpoint | 2 | st_RampSoakRecipeToSet.Steps[4].Setpoint | Ramp/Soak Step #4 to set: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].StepActive | 32 | st_RampSoakRecipeToSet.Steps[4].StepActive | Ramp/Soak Step #4 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].StepDuration | 8 | st_RampSoakRecipeToSet.Steps[4].StepDuration | Ramp/Soak Step #4 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].TempRateLimit | 25 | st_RampSoakRecipeToSet.Steps[4].TemperatureRateLimit | Ramp/Soak Step #4 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].TimedRateLimit | 8 | st_RampSoakRecipeToSet.Steps[4].TimedRateLimit | Ramp/Soak Step #4 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[4].TriggerForNext |  | st_RampSoakRecipeToSet.Steps[4].TriggerForNext | Ramp/Soak Step #4 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5] |  | st_RampSoakRecipeToSet.Steps[5] | Ramp/Soak Step #5 parameters.
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].LimitStartsAtPV | 32 | st_RampSoakRecipeToSet.Steps[5].LimitStartsAtProcessValue | Ramp/Soak Step #5 to set: FALSE=Temp- or Time-limited initial interim setpoint based on previous step's setpoint; TRUE=Temp- or time-limited initial interim setpoint based on process value upon initiation of the step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].NextAction |  | st_RampSoakRecipeToSet.Steps[5].NextAction | Ramp/Soak Step #5 to set: 0=Nothing (keep running); 1=Goto next step; 2=Cooldown unit; 3=Shutdown unit; 4=Return to Main Setpoint; 5=Return to Alternate Setpoint. | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].NextStep |  | st_RampSoakRecipeToSet.Steps[5].NextStep | Ramp/Soak Step #5 to set: The next step number (if applicable, based on next action). | <enumeration>
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].Setpoint | 2 | st_RampSoakRecipeToSet.Steps[5].Setpoint | Ramp/Soak Step #5 to set: Setpoint of the step. In units of °C. | °C
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].StepActive | 32 | st_RampSoakRecipeToSet.Steps[5].StepActive | Ramp/Soak Step #5 to set: FALSE=Inactive step; TRUE=Active step. | No/Yes
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].StepDuration | 8 | st_RampSoakRecipeToSet.Steps[5].StepDuration | Ramp/Soak Step #5 to set: Duration of the step, delay, or other time element for the step. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].TempRateLimit | 25 | st_RampSoakRecipeToSet.Steps[5].TemperatureRateLimit | Ramp/Soak Step #5 to set: 0=Unlimited; Non-zero=Temp Rate Limit over time. In units of °C/hour. | °C/hour
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].TimedRateLimit | 8 | st_RampSoakRecipeToSet.Steps[5].TimedRateLimit | Ramp/Soak Step #5 to set: 0=Unlimited; Non-zero=Ramp up to setpoint linearly over this time period. In units of seconds. | seconds
| TRUE | RAMP_SOAK | st_RampSoakRecipeToSet.Steps[5].TriggerForNext |  | st_RampSoakRecipeToSet.Steps[5].TriggerForNext | Ramp/Soak Step #5 to set: 0=Contact closure (rising edge); 1=Contact closure (rising edge) + delay; 2=Contact open (falling edge); 3=Contact open (falling edge) + delay; 4=Time; 5=Network trigger; 6=Steady-state; 7=Steady-state + delay; 8=Setpoint; 9=Setpoint + delay. | <enumeration>
HMI Display Values
| TRUE | DISPLAY | r_HD_SupplyTemp |  | r_HD_SupplyTemperature | This is the value shown on the touchscreen for "To Process Temperature". In units of °C.
| TRUE | DISPLAY | r_HD_SupplyTemp.Implemented | 42 | r_HD_SupplyTemperature.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_SupplyTemp.Value | 2 | r_HD_SupplyTemperature.Value | This is the value shown on the touchscreen for "To Process Temperature". In units of °C. | °C
| TRUE | DISPLAY | r_HD_SupplyTemp.Minimum | 2 | r_HD_SupplyTemperature.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_SupplyTemp.Maximum | 2 | r_HD_SupplyTemperature.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_SupplyTemp.Error |  | r_HD_SupplyTemperature.Error | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_ReturnTemp |  | r_HD_ReturnTemperature | This is the value shown on the touchscreen for "From Process Temperature". In units of °C.
| TRUE | DISPLAY | r_HD_ReturnTemp.Implemented | 42 | r_HD_ReturnTemperature.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_ReturnTemp.Value | 2 | r_HD_ReturnTemperature.Value | This is the value shown on the touchscreen for "From Process Temperature". In units of °C. | °C
| TRUE | DISPLAY | r_HD_ReturnTemp.Minimum | 2 | r_HD_ReturnTemperature.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_ReturnTemp.Maximum | 2 | r_HD_ReturnTemperature.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_ReturnTemp.Error |  | r_HD_ReturnTemperature.Error | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_SupplyReturnAvgTemp |  | r_HD_SupplyReturnAverageTemperature | This is the value shown on the touchscreen for "To/From Average Temperature". In units °C.
| TRUE | DISPLAY | r_HD_SupplyReturnAvgTemp.Implemented | 42 | r_HD_SupplyReturnAverageTemperature.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_SupplyReturnAvgTemp.Value | 2 | r_HD_SupplyReturnAverageTemperature.Value | This is the value shown on the touchscreen for "To/From Average Temperature". In units °C. | °C
| TRUE | DISPLAY | r_HD_SupplyReturnAvgTemp.Minimum | 2 | r_HD_SupplyReturnAverageTemperature.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_SupplyReturnAvgTemp.Maximum | 2 | r_HD_SupplyReturnAverageTemperature.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_SupplyReturnAvgTemp.Error |  | r_HD_SupplyReturnAverageTemperature.Error | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_RemoteTemp |  | r_HD_RemoteTemperature | This is the value shown on the touchscreen for "Remote Temperature". In units of °C.
| TRUE | DISPLAY | r_HD_RemoteTemp.Implemented | 42 | r_HD_RemoteTemperature.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_RemoteTemp.Value | 2 | r_HD_RemoteTemperature.Value | This is the value shown on the touchscreen for "Remote Temperature". In units of °C. | °C
| TRUE | DISPLAY | r_HD_RemoteTemp.Minimum | 2 | r_HD_RemoteTemperature.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_RemoteTemp.Maximum | 2 | r_HD_RemoteTemperature.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_RemoteTemp.Error |  | r_HD_RemoteTemperature.Error | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_Flowrate |  | r_HD_Flowrate | This is the value shown on the touchscreen for "Flowrate (analog)". In units of gpm.
| TRUE | DISPLAY | r_HD_Flowrate.Implemented | 42 | r_HD_Flowrate.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_Flowrate.Value | 5 | r_HD_Flowrate.Value | This is the value shown on the touchscreen for "Flowrate (analog)". In units of gpm. | gpm
| TRUE | DISPLAY | r_HD_Flowrate.Minimum | 5 | r_HD_Flowrate.Minimum | The minimum permitted value. | gpm
| TRUE | DISPLAY | r_HD_Flowrate.Maximum | 5 | r_HD_Flowrate.Maximum | The maximum permitted value. | gpm
| TRUE | DISPLAY | r_HD_Flowrate.Error |  | r_HD_Flowrate.Error | Describes if value is valid: 10=No Error; 5=High Circuit Fault; 6=Low Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_EstimatedFlowrate |  | r_HD_EstimatedFlowrate | This is the value shown on the touchscreen for "Estimated Flowrate". In units of gpm.
| TRUE | DISPLAY | r_HD_EstimatedFlowrate.Implemented | 42 | r_HD_EstimatedFlowrate.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_EstimatedFlowrate.Value | 5 | r_HD_EstimatedFlowrate.Value | This is the value shown on the touchscreen for "Estimated Flowrate". In units of gpm. | gpm
| TRUE | DISPLAY | r_HD_EstimatedFlowrate.Minimum | 5 | r_HD_EstimatedFlowrate.Minimum | The minimum permitted value. | gpm
| TRUE | DISPLAY | r_HD_EstimatedFlowrate.Maximum | 5 | r_HD_EstimatedFlowrate.Maximum | The maximum permitted value. | gpm
| TRUE | DISPLAY | r_HD_EstimatedFlowrate.Error |  | r_HD_EstimatedFlowrate.Error | Describes if value is valid: 10=No Error; 3=Not Currently Active; 8=No Calibration Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_SupplyPress |  | r_HD_SupplyPressure | This is the value shown on the touchscreen for "To Process Pressure". In units of psi.
| TRUE | DISPLAY | r_HD_SupplyPress.Implemented | 42 | r_HD_SupplyPressure.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_SupplyPress.Value | 13 | r_HD_SupplyPressure.Value | This is the value shown on the touchscreen for "To Process Pressure". In units of psi. | psi
| TRUE | DISPLAY | r_HD_SupplyPress.Minimum | 13 | r_HD_SupplyPressure.Minimum | The minimum permitted value. | psi
| TRUE | DISPLAY | r_HD_SupplyPress.Maximum | 13 | r_HD_SupplyPressure.Maximum | The maximum permitted value. | psi
| TRUE | DISPLAY | r_HD_SupplyPress.Error |  | r_HD_SupplyPressure.Error | Describes if value is valid: 10=No Error; 5=High Circuit Fault; 6=Low Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_ReturnPress |  | r_HD_ReturnPressure | This is the value shown on the touchscreen for "From Process Pressure". In units of psi.
| TRUE | DISPLAY | r_HD_ReturnPress.Implemented | 42 | r_HD_ReturnPressure.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_ReturnPress.Value | 13 | r_HD_ReturnPressure.Value | This is the value shown on the touchscreen for "From Process Pressure". In units of psi. | psi
| TRUE | DISPLAY | r_HD_ReturnPress.Minimum | 13 | r_HD_ReturnPressure.Minimum | The minimum permitted value. | psi
| TRUE | DISPLAY | r_HD_ReturnPress.Maximum | 13 | r_HD_ReturnPressure.Maximum | The maximum permitted value. | psi
| TRUE | DISPLAY | r_HD_ReturnPress.Error |  | r_HD_ReturnPressure.Error | Describes if value is valid: 10=No Error; 5=High Circuit Fault; 6=Low Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_HeatCool_Pct |  | r_HD_HeatCool_Percent | This is the value shown on the touchscreen for "Heat / Cool Amount (Instantaneous)". In units of %.
| TRUE | DISPLAY | r_HD_HeatCool_Pct.Implemented | 42 | r_HD_HeatCool_Percent.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_HeatCool_Pct.Value | 11 | r_HD_HeatCool_Percent.Value | This is the value shown on the touchscreen for "Heat / Cool Amount (Instantaneous)". In units of %. | %
| TRUE | DISPLAY | r_HD_HeatCool_Pct.Minimum | 11 | r_HD_HeatCool_Percent.Minimum | The minimum permitted value. | %
| TRUE | DISPLAY | r_HD_HeatCool_Pct.Maximum | 11 | r_HD_HeatCool_Percent.Maximum | The maximum permitted value. | %
| TRUE | DISPLAY | r_HD_HeatCool_Pct.Error |  | r_HD_HeatCool_Percent.Error | Describes if value is valid: 10=0% Heat/Cool; 0=Heat/Cool Off; 1=Heating, 2=Cooling, 3=Maximum Cooling. | <enumeration>
| TRUE | DISPLAY | r_HD_Heat_Pct |  | r_HD_Heat_Percent | This is the value shown on the touchscreen for "Heat Amount (Instantaneous)". In units of %.
| TRUE | DISPLAY | r_HD_Heat_Pct.Implemented | 42 | r_HD_Heat_Percent.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_Heat_Pct.Value | 11 | r_HD_Heat_Percent.Value | This is the value shown on the touchscreen for "Heat Amount (Instantaneous)". In units of %. | %
| TRUE | DISPLAY | r_HD_Heat_Pct.Minimum | 11 | r_HD_Heat_Percent.Minimum | The minimum permitted value. | %
| TRUE | DISPLAY | r_HD_Heat_Pct.Maximum | 11 | r_HD_Heat_Percent.Maximum | The maximum permitted value. | %
| TRUE | DISPLAY | r_HD_Heat_Pct.Error |  | r_HD_Heat_Percent.Error | Describes if value is valid: 10=No error; 0=Error | <enumeration>
| TRUE | DISPLAY | r_HD_Cool_Pct |  | r_HD_Cool_Percent | This is the value shown on the touchscreen for "Cool Amount (Instantaneous)". In units of %.
| TRUE | DISPLAY | r_HD_Cool_Pct.Implemented | 42 | r_HD_Cool_Percent.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_Cool_Pct.Value | 11 | r_HD_Cool_Percent.Value | This is the value shown on the touchscreen for "Cool Amount (Instantaneous)". In units of %. | %
| TRUE | DISPLAY | r_HD_Cool_Pct.Minimum | 11 | r_HD_Cool_Percent.Minimum | The minimum permitted value. | %
| TRUE | DISPLAY | r_HD_Cool_Pct.Maximum | 11 | r_HD_Cool_Percent.Maximum | The maximum permitted value. | %
| TRUE | DISPLAY | r_HD_Cool_Pct.Error |  | r_HD_Cool_Percent.Error | Describes if value is valid: 10=No error; 0=Error | <enumeration>
| FALSE | DISPLAY | r_HD_NetworkProcessTemp |  | r_HD_NetworkProcessTemperature | Not currently implemented.
| FALSE | DISPLAY | r_HD_NetworkProcessTemp.Implemented | 42 | r_HD_NetworkProcessTemperature.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_NetworkProcessTemp.Value | 2 | r_HD_NetworkProcessTemperature.Value | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_NetworkProcessTemp.Minimum | 2 | r_HD_NetworkProcessTemperature.Minimum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_NetworkProcessTemp.Maximum | 2 | r_HD_NetworkProcessTemperature.Maximum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_NetworkProcessTemp.Error |  | r_HD_NetworkProcessTemperature.Error | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | r_HD_AnalogProcessTemp |  | r_HD_AnalogProcessTemperature | Not currently implemented.
| FALSE | DISPLAY | r_HD_AnalogProcessTemp.Implemented | 42 | r_HD_AnalogProcessTemperature.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_AnalogProcessTemp.Value | 2 | r_HD_AnalogProcessTemperature.Value | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_AnalogProcessTemp.Minimum | 2 | r_HD_AnalogProcessTemperature.Minimum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_AnalogProcessTemp.Maximum | 2 | r_HD_AnalogProcessTemperature.Maximum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_AnalogProcessTemp.Error |  | r_HD_AnalogProcessTemperature.Error | Not currently implemented. | <enumeration>
| TRUE | DISPLAY | r_HD_ActiveProcTemp |  | r_HD_ActiveProcessTemperature | This is the value shown on the touchscreen for "Active Process Temperature". Units of °C.
| TRUE | DISPLAY | r_HD_ActiveProcTemp.Implemented | 42 | r_HD_ActiveProcessTemperature.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_ActiveProcTemp.Value | 2 | r_HD_ActiveProcessTemperature.Value | This is the value shown on the touchscreen for "Active Process Temperature". Units of °C. | °C
| TRUE | DISPLAY | r_HD_ActiveProcTemp.Minimum | 2 | r_HD_ActiveProcessTemperature.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_ActiveProcTemp.Maximum | 2 | r_HD_ActiveProcessTemperature.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_ActiveProcTemp.Error |  | r_HD_ActiveProcessTemperature.Error | Describes if value is valid: 10=No Error; 1=Open Circuit Fault; 2=Short Circuit Fault; 3=Other Fault; 4=Not Used; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_RampSoakSetpoint |  | r_HD_RampSoakSetpoint | This is the value shown on the touchscreen for "Ramp/Soak Setpoint". In units of °C.
| TRUE | DISPLAY | r_HD_RampSoakSetpoint.Implemented | 42 | r_HD_RampSoakSetpoint.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_RampSoakSetpoint.Value | 2 | r_HD_RampSoakSetpoint.Value | This is the value shown on the touchscreen for "Ramp/Soak Setpoint". In units of °C. | °C
| TRUE | DISPLAY | r_HD_RampSoakSetpoint.Minimum | 2 | r_HD_RampSoakSetpoint.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_RampSoakSetpoint.Maximum | 2 | r_HD_RampSoakSetpoint.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_RampSoakSetpoint.Error |  | r_HD_RampSoakSetpoint.Error | Describes if value is valid: 10=No Error; 4=Not Used; 0=Error. | <enumeration>
| FALSE | DISPLAY | r_HD_AnalogSetpoint |  | r_HD_AnalogSetpoint | Not currently implemented.
| FALSE | DISPLAY | r_HD_AnalogSetpoint.Implemented | 42 | r_HD_AnalogSetpoint.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_AnalogSetpoint.Value | 2 | r_HD_AnalogSetpoint.Value | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_AnalogSetpoint.Minimum | 2 | r_HD_AnalogSetpoint.Minimum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_AnalogSetpoint.Maximum | 2 | r_HD_AnalogSetpoint.Maximum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_AnalogSetpoint.Error |  | r_HD_AnalogSetpoint.Error | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | r_HD_NetworkSetpoint |  | r_HD_NetworkSetpoint | Not currently implemented.
| FALSE | DISPLAY | r_HD_NetworkSetpoint.Implemented | 42 | r_HD_NetworkSetpoint.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_NetworkSetpoint.Value | 2 | r_HD_NetworkSetpoint.Value | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_NetworkSetpoint.Minimum | 2 | r_HD_NetworkSetpoint.Minimum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_NetworkSetpoint.Maximum | 2 | r_HD_NetworkSetpoint.Maximum | Not currently implemented. | °C
| FALSE | DISPLAY | r_HD_NetworkSetpoint.Error |  | r_HD_NetworkSetpoint.Error | Not currently implemented. | <enumeration>
| TRUE | DISPLAY | r_HD_SuggestedSetpoint |  | r_HD_SuggestedSetpoint | This is the value shown on the touchscreen for suggested setpoint if pressure too low. In units of °C.
| TRUE | DISPLAY | r_HD_SuggestedSetpoint.Implemented | 42 | r_HD_SuggestedSetpoint.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_SuggestedSetpoint.Value | 2 | r_HD_SuggestedSetpoint.Value | This is the value shown on the touchscreen for suggested setpoint if pressure too low. In units of °C. | °C
| TRUE | DISPLAY | r_HD_SuggestedSetpoint.Minimum | 2 | r_HD_SuggestedSetpoint.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_SuggestedSetpoint.Maximum | 2 | r_HD_SuggestedSetpoint.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_SuggestedSetpoint.Error |  | r_HD_SuggestedSetpoint.Error | Describes if value is valid: 10=No Error; 9=Value not currently useful; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_EffectiveProcValue |  | r_HD_EffectiveProcessValue | This is the value shown on the touchscreen for the process value being used to drive the PID loop. In units of °C.
| TRUE | DISPLAY | r_HD_EffectiveProcValue.Implemented | 42 | r_HD_EffectiveProcessValue.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_EffectiveProcValue.Value | 2 | r_HD_EffectiveProcessValue.Value | This is the value shown on the touchscreen for the process value being used to drive the PID loop. In units of °C. | °C
| TRUE | DISPLAY | r_HD_EffectiveProcValue.Minimum | 2 | r_HD_EffectiveProcessValue.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_EffectiveProcValue.Maximum | 2 | r_HD_EffectiveProcessValue.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_EffectiveProcValue.Error |  | r_HD_EffectiveProcessValue.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveProcValueSource |  | n_HD_EffectiveProcessValueSource | This is the value shown on the touchscreen for the enumerated source for the filtered effective process value. 0="To Process RTD", 1="From Process RTD", 2="To/From RTD Avg", 3="Remote RTD", 4="Analog Signal", 5="Network"
| TRUE | DISPLAY | n_HD_EffectiveProcValueSource.Implemented | 42 | n_HD_EffectiveProcessValueSource.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | n_HD_EffectiveProcValueSource.Value |  | n_HD_EffectiveProcessValueSource.Value | This is the value shown on the touchscreen for the enumerated source for the filtered effective process value. 0="To Process RTD", 1="From Process RTD", 2="To/From RTD Avg", 3="Remote RTD", 4="Analog Signal", 5="Network" | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveProcValueSource.Minimum |  | n_HD_EffectiveProcessValueSource.Minimum | The minimum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveProcValueSource.Maximum |  | n_HD_EffectiveProcessValueSource.Maximum | The maximum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveProcValueSource.Error |  | n_HD_EffectiveProcessValueSource.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_FilteredEffectiveProcValue |  | r_HD_FilteredEffectiveProcessValue | This is the value shown on the touchscreen for "Filtered Effective Process Value". In units of °C.
| TRUE | DISPLAY | r_HD_FilteredEffectiveProcValue.Implemented | 42 | r_HD_FilteredEffectiveProcessValue.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_FilteredEffectiveProcValue.Value | 2 | r_HD_FilteredEffectiveProcessValue.Value | This is the value shown on the touchscreen for "Filtered Effective Process Value". In units of °C. | °C
| TRUE | DISPLAY | r_HD_FilteredEffectiveProcValue.Minimum | 2 | r_HD_FilteredEffectiveProcessValue.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_FilteredEffectiveProcValue.Maximum | 2 | r_HD_FilteredEffectiveProcessValue.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_FilteredEffectiveProcValue.Error |  | r_HD_FilteredEffectiveProcessValue.Error | Describes if value is valid: 10=No Error; 3=Selected Setpoint Source is providing a bad value; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_EffectiveSetpoint |  | r_HD_EffectiveSetpoint | This is the value shown on the touchscreen for the setpoint value being used to drive the PID loop. In units of °C.
| TRUE | DISPLAY | r_HD_EffectiveSetpoint.Implemented | 42 | r_HD_EffectiveSetpoint.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_EffectiveSetpoint.Value | 2 | r_HD_EffectiveSetpoint.Value | This is the value shown on the touchscreen for the setpoint value being used to drive the PID loop. In units of °C. | °C
| TRUE | DISPLAY | r_HD_EffectiveSetpoint.Minimum | 2 | r_HD_EffectiveSetpoint.Minimum | The minimum permitted value. | °C
| TRUE | DISPLAY | r_HD_EffectiveSetpoint.Maximum | 2 | r_HD_EffectiveSetpoint.Maximum | The maximum permitted value. | °C
| TRUE | DISPLAY | r_HD_EffectiveSetpoint.Error |  | r_HD_EffectiveSetpoint.Error | Describes if value is valid: 10=No Error; 4=Not Used; 5=High Circuit Fault; 6=Low Circuit Fault; 7=Heartbeat Error; 3=Other Fault; 0=Error. | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveSetpointSource |  | n_HD_EffectiveSetpointSource | This is the value shown on the touchscreen for the enumerated source for the effective setpoint value. 0=Main; 1=Alternative; 2=Ramp/Soak; 3=Analog Signal; 4=Network
| TRUE | DISPLAY | n_HD_EffectiveSetpointSource.Implemented | 42 | n_HD_EffectiveSetpointSource.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | n_HD_EffectiveSetpointSource.Value |  | n_HD_EffectiveSetpointSource.Value | This is the value shown on the touchscreen for the enumerated source for the effective setpoint value. 0=Main; 1=Alternative; 2=Ramp/Soak; 3=Analog Signal; 4=Network | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveSetpointSource.Minimum |  | n_HD_EffectiveSetpointSource.Minimum | The minimum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveSetpointSource.Maximum |  | n_HD_EffectiveSetpointSource.Maximum | The maximum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_EffectiveSetpointSource.Error |  | n_HD_EffectiveSetpointSource.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_PID_Multiplier |  | r_HD_PID_Multiplier | This is the value shown on the touchscreen for the modification factor on the PID output to compensate for non-linearities in the system.
| TRUE | DISPLAY | r_HD_PID_Multiplier.Implemented | 42 | r_HD_PID_Multiplier.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_PID_Multiplier.Value |  | r_HD_PID_Multiplier.Value | This is the value shown on the touchscreen for the modification factor on the PID output to compensate for non-linearities in the system. | N/A
| TRUE | DISPLAY | r_HD_PID_Multiplier.Minimum |  | r_HD_PID_Multiplier.Minimum | The minimum permitted value. | N/A
| TRUE | DISPLAY | r_HD_PID_Multiplier.Maximum |  | r_HD_PID_Multiplier.Maximum | The maximum permitted value. | N/A
| TRUE | DISPLAY | r_HD_PID_Multiplier.Error |  | r_HD_PID_Multiplier.Error | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_PID_ProportionalTerm |  | r_HD_PID_ProportionalTerm | This is the value shown on the touchscreen for the proportional contribution from the PID loop. In units of %.
| TRUE | DISPLAY | r_HD_PID_ProportionalTerm.Implemented | 42 | r_HD_PID_ProportionalTerm.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_PID_ProportionalTerm.Value | 11 | r_HD_PID_ProportionalTerm.Value | This is the value shown on the touchscreen for the proportional contribution from the PID loop. In units of %. | %
| TRUE | DISPLAY | r_HD_PID_ProportionalTerm.Minimum | 11 | r_HD_PID_ProportionalTerm.Minimum | The minimum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_ProportionalTerm.Maximum | 11 | r_HD_PID_ProportionalTerm.Maximum | The maximum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_ProportionalTerm.Error |  | r_HD_PID_ProportionalTerm.Error | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_PID_IntegralTerm |  | r_HD_PID_IntegralTerm | This is the value shown on the touchscreen for the integral contribution from the PID loop. In units of %.
| TRUE | DISPLAY | r_HD_PID_IntegralTerm.Implemented | 42 | r_HD_PID_IntegralTerm.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_PID_IntegralTerm.Value | 11 | r_HD_PID_IntegralTerm.Value | This is the value shown on the touchscreen for the integral contribution from the PID loop. In units of %. | %
| TRUE | DISPLAY | r_HD_PID_IntegralTerm.Minimum | 11 | r_HD_PID_IntegralTerm.Minimum | The minimum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_IntegralTerm.Maximum | 11 | r_HD_PID_IntegralTerm.Maximum | The maximum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_IntegralTerm.Error |  | r_HD_PID_IntegralTerm.Error | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_PID_DerivativeTerm |  | r_HD_PID_DerivativeTerm | This is the value shown on the touchscreen for the derivative contribution from the PID loop. In units of %.
| TRUE | DISPLAY | r_HD_PID_DerivativeTerm.Implemented | 42 | r_HD_PID_DerivativeTerm.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_PID_DerivativeTerm.Value | 11 | r_HD_PID_DerivativeTerm.Value | This is the value shown on the touchscreen for the derivative contribution from the PID loop. In units of %. | %
| TRUE | DISPLAY | r_HD_PID_DerivativeTerm.Minimum | 11 | r_HD_PID_DerivativeTerm.Minimum | The minimum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_DerivativeTerm.Maximum | 11 | r_HD_PID_DerivativeTerm.Maximum | The maximum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_DerivativeTerm.Error |  | r_HD_PID_DerivativeTerm.Error | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_PID_Error |  | r_HD_PID_Error | This is the value shown on the touchscreen for the difference between the setpoint and the process value from the PID loop. In units of Δ°C.
| TRUE | DISPLAY | r_HD_PID_Error.Implemented | 42 | r_HD_PID_Error.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_PID_Error.Value | 4 | r_HD_PID_Error.Value | This is the value shown on the touchscreen for the difference between the setpoint and the process value from the PID loop. In units of Δ°C. | Δ°C
| TRUE | DISPLAY | r_HD_PID_Error.Minimum | 4 | r_HD_PID_Error.Minimum | The minimum permitted value. | Δ°C
| TRUE | DISPLAY | r_HD_PID_Error.Maximum | 4 | r_HD_PID_Error.Maximum | The maximum permitted value. | Δ°C
| TRUE | DISPLAY | r_HD_PID_Error.Error |  | r_HD_PID_Error.Error | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_PID_RawLoopOutput |  | r_HD_PID_RawLoopOutput | This is the value shown on the touchscreen for the raw output from the PID loop. In units of %.
| TRUE | DISPLAY | r_HD_PID_RawLoopOutput.Implemented | 42 | r_HD_PID_RawLoopOutput.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_PID_RawLoopOutput.Value | 11 | r_HD_PID_RawLoopOutput.Value | This is the value shown on the touchscreen for the raw output from the PID loop. In units of %. | %
| TRUE | DISPLAY | r_HD_PID_RawLoopOutput.Minimum | 11 | r_HD_PID_RawLoopOutput.Minimum | The minimum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_RawLoopOutput.Maximum | 11 | r_HD_PID_RawLoopOutput.Maximum | The maximum permitted value. | %
| TRUE | DISPLAY | r_HD_PID_RawLoopOutput.Error |  | r_HD_PID_RawLoopOutput.Error | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| TRUE | DISPLAY | b_HD_PID_SteadyState |  | b_HD_PID_SteadyState | This is the value shown on the touchscreen for flag indicating if the unit is operating under smooth, steady-state temperature regulation. 0=pid not in steady-state operation; 1=pid in steady-state operation.
| TRUE | DISPLAY | b_HD_PID_SteadyState.Implemented | 42 | b_HD_PID_SteadyState.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | b_HD_PID_SteadyState.Value | 42 | b_HD_PID_SteadyState.Value | This is the value shown on the touchscreen for flag indicating if the unit is operating under smooth, steady-state temperature regulation. 0=pid not in steady-state operation; 1=pid in steady-state operation. | Off/On
| TRUE | DISPLAY | b_HD_PID_SteadyState.Error |  | b_HD_PID_SteadyState.Error | Describes if value is valid: 10=No Error; 9=Not currently relevant; 0=Error. | <enumeration>
| FALSE | DISPLAY | n_HD_AT_State |  | n_HD_Autotune_State | Not currently implemented.
| FALSE | DISPLAY | n_HD_AT_State.Implemented | 42 | n_HD_Autotune_State.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | n_HD_AT_State.Value | 11 | n_HD_Autotune_State.Value | Not currently implemented. | %
| FALSE | DISPLAY | n_HD_AT_State.Minimum | 11 | n_HD_Autotune_State.Minimum | Not currently implemented. | %
| FALSE | DISPLAY | n_HD_AT_State.Maximum | 11 | n_HD_Autotune_State.Maximum | Not currently implemented. | %
| FALSE | DISPLAY | n_HD_AT_State.Error |  | n_HD_Autotune_State.Error | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | r_HD_AT_Output |  | r_HD_Autotune_Output | Not currently implemented.
| FALSE | DISPLAY | r_HD_AT_Output.Implemented | 42 | r_HD_Autotune_Output.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_AT_Output.Value | 11 | r_HD_Autotune_Output.Value | Not currently implemented. | %
| FALSE | DISPLAY | r_HD_AT_Output.Minimum | 11 | r_HD_Autotune_Output.Minimum | Not currently implemented. | %
| FALSE | DISPLAY | r_HD_AT_Output.Maximum | 11 | r_HD_Autotune_Output.Maximum | Not currently implemented. | %
| FALSE | DISPLAY | r_HD_AT_Output.Error |  | r_HD_Autotune_Output.Error | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | r_HD_AT_NewP_Band |  | r_HD_Autotune_NewProportionalBand | Not currently implemented.
| FALSE | DISPLAY | r_HD_AT_NewP_Band.Implemented | 42 | r_HD_Autotune_NewProportionalBand.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_AT_NewP_Band.Value | 4 | r_HD_Autotune_NewProportionalBand.Value | Not currently implemented. | Δ°C
| FALSE | DISPLAY | r_HD_AT_NewP_Band.Minimum | 4 | r_HD_Autotune_NewProportionalBand.Minimum | Not currently implemented. | Δ°C
| FALSE | DISPLAY | r_HD_AT_NewP_Band.Maximum | 4 | r_HD_Autotune_NewProportionalBand.Maximum | Not currently implemented. | Δ°C
| FALSE | DISPLAY | r_HD_AT_NewP_Band.Error |  | r_HD_Autotune_NewProportionalBand.Error | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | r_HD_AT_NewIntegralGain |  | r_HD_Autotune_NewIntegralGain | Not currently implemented.
| FALSE | DISPLAY | r_HD_AT_NewIntegralGain.Implemented | 42 | r_HD_Autotune_NewIntegralGain.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_AT_NewIntegralGain.Value | 8 | r_HD_Autotune_NewIntegralGain.Value | Not currently implemented. | seconds
| FALSE | DISPLAY | r_HD_AT_NewIntegralGain.Minimum | 8 | r_HD_Autotune_NewIntegralGain.Minimum | Not currently implemented. | seconds
| FALSE | DISPLAY | r_HD_AT_NewIntegralGain.Maximum | 8 | r_HD_Autotune_NewIntegralGain.Maximum | Not currently implemented. | seconds
| FALSE | DISPLAY | r_HD_AT_NewIntegralGain.Error |  | r_HD_Autotune_NewIntegralGain.Error | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | r_HD_AT_NewDerivativeGain |  | r_HD_Autotune_NewDerivativeGain | Not currently implemented.
| FALSE | DISPLAY | r_HD_AT_NewDerivativeGain.Implemented | 42 | r_HD_Autotune_NewDerivativeGain.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | r_HD_AT_NewDerivativeGain.Value | 8 | r_HD_Autotune_NewDerivativeGain.Value | Not currently implemented. | seconds
| FALSE | DISPLAY | r_HD_AT_NewDerivativeGain.Minimum | 8 | r_HD_Autotune_NewDerivativeGain.Minimum | Not currently implemented. | seconds
| FALSE | DISPLAY | r_HD_AT_NewDerivativeGain.Maximum | 8 | r_HD_Autotune_NewDerivativeGain.Maximum | Not currently implemented. | seconds
| FALSE | DISPLAY | r_HD_AT_NewDerivativeGain.Error |  | r_HD_Autotune_NewDerivativeGain.Error | Not currently implemented. | <enumeration>
| TRUE | DISPLAY | n_HD_MSM_State |  | n_HD_MasterStateMachine_State | This is the value shown on the touchscreen for MSM State enumeration. 0="Unknown"; 1="Booting"; 2="Starting"; 3="Preparing to Stop"; 4="Stopped"; 5=Preparing to Vent"; 6="Valve Vent"; 7="Pump/Valve Vent"; 8="Preparing to Run"; 9="Running"; 10="Low Pressure Pause"; 11="Auto Cool Stop"; 12="Mold Purge Active"; 13="User Configuration"; 14="Diagnostics"; 15="Factory Configuration"; 16="Preparing to Alarm"; 17="Alarm-Resettable";18=Alarm-Cycle Power"; 19="Alarm-Overtemperature"; 20="Alarm Resetting"; 21="Rebooting".
| TRUE | DISPLAY | n_HD_MSM_State.Implemented | 42 | n_HD_MasterStateMachine_State.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | n_HD_MSM_State.Value |  | n_HD_MasterStateMachine_State.Value | This is the value shown on the touchscreen for MSM State enumeration. 0="Unknown"; 1="Booting"; 2="Starting"; 3="Preparing to Stop"; 4="Stopped"; 5=Preparing to Vent"; 6="Valve Vent"; 7="Pump/Valve Vent"; 8="Preparing to Run"; 9="Running"; 10="Low Pressure Pause"; 11="Auto Cool Stop"; 12="Mold Purge Active"; 13="User Configuration"; 14="Diagnostics"; 15="Factory Configuration"; 16="Preparing to Alarm"; 17="Alarm-Resettable";18=Alarm-Cycle Power"; 19="Alarm-Overtemperature"; 20="Alarm Resetting"; 21="Rebooting". | <enumeration>
| TRUE | DISPLAY | n_HD_MSM_State.Minimum |  | n_HD_MasterStateMachine_State.Minimum | The minimum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_MSM_State.Maximum |  | n_HD_MasterStateMachine_State.Maximum | The maximum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_MSM_State.Error |  | n_HD_MasterStateMachine_State.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | n_HD_TSM_State |  | n_HD_TemperatureStateMachine_State | This is the value shown on the touchscreen for TSM State enumeration. 0=Unknown; 1=Boot; 2=Init; 3=Stop; 4=Vent; 5=SV: No Heat/Cool; 6=SV: Heat; 7=SV: Cool; 8=FV: No Heat/Cool; 9=FV: Heat; 10=FV: Less Cool; 11=FV: Less Cool, Prepare to Open; 12=FV: More Cool; 13=FV: More Cool, Prepare to Close; 14=Mod Valve: No Heat/Cool; 15=MV: Heat; 16=MV: Cool; 17=Emergency Cooling (all valve types).
| TRUE | DISPLAY | n_HD_TSM_State.Implemented | 42 | n_HD_TemperatureStateMachine_State.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | n_HD_TSM_State.Value |  | n_HD_TemperatureStateMachine_State.Value | This is the value shown on the touchscreen for TSM State enumeration. 0=Unknown; 1=Boot; 2=Init; 3=Stop; 4=Vent; 5=SV: No Heat/Cool; 6=SV: Heat; 7=SV: Cool; 8=FV: No Heat/Cool; 9=FV: Heat; 10=FV: Less Cool; 11=FV: Less Cool, Prepare to Open; 12=FV: More Cool; 13=FV: More Cool, Prepare to Close; 14=Mod Valve: No Heat/Cool; 15=MV: Heat; 16=MV: Cool; 17=Emergency Cooling (all valve types). | <enumeration>
| TRUE | DISPLAY | n_HD_TSM_State.Minimum |  | n_HD_TemperatureStateMachine_State.Minimum | The minimum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_TSM_State.Maximum |  | n_HD_TemperatureStateMachine_State.Maximum | The maximum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_TSM_State.Error |  | n_HD_TemperatureStateMachine_State.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| FALSE | DISPLAY | n_HD_NetworkStatus |  | n_HD_NetworkStatus | Not currently implemented.
| FALSE | DISPLAY | n_HD_NetworkStatus.Implemented | 42 | n_HD_NetworkStatus.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | n_HD_NetworkStatus.Value |  | n_HD_NetworkStatus.Value | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | n_HD_NetworkStatus.Minimum |  | n_HD_NetworkStatus.Minimum | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | n_HD_NetworkStatus.Maximum |  | n_HD_NetworkStatus.Maximum | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | n_HD_NetworkStatus.Error |  | n_HD_NetworkStatus.Error | Not currently implemented. | <enumeration>
| FALSE | DISPLAY | n_HD_ModbusErrorCode |  | n_HD_ModbusErrorCode | Not currently implemented.
| FALSE | DISPLAY | n_HD_ModbusErrorCode.Implemented | 42 | n_HD_ModbusErrorCode.Implemented | Not currently implemented. | Off/On
| FALSE | DISPLAY | n_HD_ModbusErrorCode.Value |  | n_HD_ModbusErrorCode.Value | Not currently implemented. | N/A
| FALSE | DISPLAY | n_HD_ModbusErrorCode.Minimum |  | n_HD_ModbusErrorCode.Minimum | Not currently implemented. | N/A
| FALSE | DISPLAY | n_HD_ModbusErrorCode.Maximum |  | n_HD_ModbusErrorCode.Maximum | Not currently implemented. | N/A
| FALSE | DISPLAY | n_HD_ModbusErrorCode.Error |  | n_HD_ModbusErrorCode.Error | Not currently implemented. | <enumeration>
| TRUE | DISPLAY | u_HD_RampSoakStep |  | u_HD_RampSoakStep | This is the value shown on the touchscreen for Ramp/Soak Step.
| TRUE | DISPLAY | u_HD_RampSoakStep.Implemented | 42 | u_HD_RampSoakStep.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | u_HD_RampSoakStep.Value | 29 | u_HD_RampSoakStep.Value | This is the value shown on the touchscreen for Ramp/Soak Step. | step
| TRUE | DISPLAY | u_HD_RampSoakStep.Minimum | 29 | u_HD_RampSoakStep.Minimum | The minimum permitted value. | step
| TRUE | DISPLAY | u_HD_RampSoakStep.Maximum | 29 | u_HD_RampSoakStep.Maximum | The maximum permitted value. | step
| TRUE | DISPLAY | u_HD_RampSoakStep.Error |  | u_HD_RampSoakStep.Error | Describes if value is valid: 10=No Error; 9=Not relevant in current machine state; 4=Not used; 0=Error. | <enumeration>
| TRUE | DISPLAY | n_HD_InterimSetpointDirection |  | n_HD_InterimSetpointDirection | This is the value shown on the touchscreen for Interim Setpoint Direction enumeration. 0=No direction; 1=Up; 2=Down.
| TRUE | DISPLAY | n_HD_InterimSetpointDirection.Implemented | 42 | n_HD_InterimSetpointDirection.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | n_HD_InterimSetpointDirection.Value |  | n_HD_InterimSetpointDirection.Value | This is the value shown on the touchscreen for Interim Setpoint Direction enumeration. 0=No direction; 1=Up; 2=Down. | <enumeration>
| TRUE | DISPLAY | n_HD_InterimSetpointDirection.Minimum |  | n_HD_InterimSetpointDirection.Minimum | The minimum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_InterimSetpointDirection.Maximum |  | n_HD_InterimSetpointDirection.Maximum | The maximum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_InterimSetpointDirection.Error |  | n_HD_InterimSetpointDirection.Error | Describes if value is valid: 10=No Error; 9=Not relevant in current machine state; 0=Error. | <enumeration>
| TRUE | DISPLAY | b_HD_RampSoakShowTime |  | b_HD_RampSoakShowTime | Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay.
| TRUE | DISPLAY | b_HD_RampSoakShowTime[1] | 32 | b_HD_RampSoakShowTime[1] | Ramp/Soak: Step #1: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| TRUE | DISPLAY | b_HD_RampSoakShowTime[2] | 32 | b_HD_RampSoakShowTime[2] | Ramp/Soak: Step #2: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| TRUE | DISPLAY | b_HD_RampSoakShowTime[3] | 32 | b_HD_RampSoakShowTime[3] | Ramp/Soak: Step #3: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| TRUE | DISPLAY | b_HD_RampSoakShowTime[4] | 32 | b_HD_RampSoakShowTime[4] | Ramp/Soak: Step #4: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| TRUE | DISPLAY | b_HD_RampSoakShowTime[5] | 32 | b_HD_RampSoakShowTime[5] | Ramp/Soak: Step #5: Describes if the Ramp/Soak time for this step is a valid field based on if that step has been configured to operate on a time delay. | No/Yes
| TRUE | DISPLAY | b_HD_RampSoakShowNextStep |  | b_HD_RampSoakShowNextStep | Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined.
| TRUE | DISPLAY | b_HD_RampSoakShowNextStep[1] | 29 | b_HD_RampSoakShowNextStep[1] | Ramp/Soak: Step #1: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| TRUE | DISPLAY | b_HD_RampSoakShowNextStep[2] | 29 | b_HD_RampSoakShowNextStep[2] | Ramp/Soak: Step #2: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| TRUE | DISPLAY | b_HD_RampSoakShowNextStep[3] | 29 | b_HD_RampSoakShowNextStep[3] | Ramp/Soak: Step #3: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| TRUE | DISPLAY | b_HD_RampSoakShowNextStep[4] | 29 | b_HD_RampSoakShowNextStep[4] | Ramp/Soak: Step #4: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| TRUE | DISPLAY | b_HD_RampSoakShowNextStep[5] | 29 | b_HD_RampSoakShowNextStep[5] | Ramp/Soak: Step #5: Describes if the Ramp/Soak step is configured with an action that requires a "next step" to be defined. | step
| TRUE | DISPLAY | u_HD_Countdown |  | u_HD_Countdown | This is the value shown on the touchscreen for countdown clock. In units of seconds. |  | Enumeration
| TRUE | DISPLAY | u_HD_Countdown.Implemented | 42 | u_HD_Countdown.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On | Enumeration
| TRUE | DISPLAY | u_HD_Countdown.Value | 8 | u_HD_Countdown.Value | This is the value shown on the touchscreen for countdown clock. In units of seconds. | seconds | Enumeration
| TRUE | DISPLAY | u_HD_Countdown.Minimum | 8 | u_HD_Countdown.Minimum | The minimum permitted value. | seconds | Enumeration
| TRUE | DISPLAY | u_HD_Countdown.Maximum | 8 | u_HD_Countdown.Maximum | The maximum permitted value. | seconds | Enumeration
| TRUE | DISPLAY | u_HD_Countdown.Error |  | u_HD_Countdown.Error | Describes if value is valid: 10=No Error; 9=Not relevant in current machine state; 0=Error. | <enumeration> | Enumeration
| TRUE | DISPLAY | u_HD_CountdownType |  | u_HD_CountdownType | This is the value shown on the touchscreen for countdown event type enumeration. 0=None; 1=Valve Vent; 2=Valve/Pump Vent; 3=Low-Pressure Ride-Through; 4=Low-Pressure Resume; 5=Mold Purge; 6=Ramp/Soak Event; 7=Auto Cool Stop; 8=Reboot; 9=Auto-Restart; 10=Mod Valve Homing;
| TRUE | DISPLAY | u_HD_CountdownType.Implemented | 42 | u_HD_CountdownType.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | u_HD_CountdownType.Value |  | u_HD_CountdownType.Value | This is the value shown on the touchscreen for countdown event type enumeration. 0=None; 1=Valve Vent; 2=Valve/Pump Vent; 3=Low-Pressure Ride-Through; 4=Low-Pressure Resume; 5=Mold Purge; 6=Ramp/Soak Event; 7=Auto Cool Stop; 8=Reboot; 9=Auto-Restart; 10=Mod Valve Homing; | <enumeration>
| TRUE | DISPLAY | u_HD_CountdownType.Minimum |  | u_HD_CountdownType.Minimum | The minimum permitted value. | <enumeration>
| TRUE | DISPLAY | u_HD_CountdownType.Maximum |  | u_HD_CountdownType.Maximum | The maximum permitted value. | <enumeration>
| TRUE | DISPLAY | u_HD_CountdownType.Error |  | u_HD_CountdownType.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | n_HD_RebootMessage |  | n_HD_RebootMessage | This is the value shown on the touchscreen for reboot message enumeration. 0="Preparing to Reboot"; 1="Loading Operator Defaults"; 2="Loading Maintenance Defaults"; 3="Changing Units"; 4="Changing Branding"; 5="Changing IO Setup"; 6="Updating Network". |  | For details, see Modbus_Status sheet.
| TRUE | DISPLAY | n_HD_RebootMessage.Implemented | 42 | n_HD_RebootMessage.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On | For details, see Modbus_Status sheet.
| TRUE | DISPLAY | n_HD_RebootMessage.Value |  | n_HD_RebootMessage.Value | This is the value shown on the touchscreen for reboot message enumeration. 0="Preparing to Reboot"; 1="Loading Operator Defaults"; 2="Loading Maintenance Defaults"; 3="Changing Units"; 4="Changing Branding"; 5="Changing IO Setup"; 6="Updating Network". | <enumeration> | For details, see Modbus_Status sheet.
| TRUE | DISPLAY | n_HD_RebootMessage.Minimum |  | n_HD_RebootMessage.Minimum | For details, see Modbus_Status sheet. | <enumeration> | For details, see Modbus_Status sheet.
| TRUE | DISPLAY | n_HD_RebootMessage.Maximum |  | n_HD_RebootMessage.Maximum | For details, see Modbus_Status sheet. | <enumeration> | For details, see Modbus_Status sheet.
| TRUE | DISPLAY | n_HD_RebootMessage.Error |  | n_HD_RebootMessage.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration> | For details, see Modbus_Status sheet.
| TRUE | DISPLAY | n_HD_Alarm |  | n_HD_Alarm | Highest Priority Alarm. 1=IO Connection Failure; 2=IO Module Link Failure; 3=IO Module Hardware Mismatch; 4=IO Module Internal Fault; 5=IO Point Failure; 6=Power Supply Voltage Low; 7=Logic Supply Voltage Low; 8=Overtemperature Fault; 9=Heater Contactor Stuck Closed; 10=Temperature Over Limit; 11=Unbranded; 12=Factory Options Not Set; 13=Electric Power Fault; 14=Pump Contactor Stuck Closed; 15=Heater Contactor Stuck Open; 16=Pump Contactor Stuck Open; 17=System Pressure Too High; 18=Electrical Panel Too Hot; 19=Temperature Under Limit; 20=Brownout Occurred; 21=Temperature Over Setting; 22=Temperature Under Setting; 23=Low Pressure Shutdown; 24=Low Pressure Too Many Events; 25=Pump Overload Tripped; 26=Flowmeter Low Flow; 27=To Proc RTD Probe Open; 28=To Proc RTD Probe Short; 29=To Proc RTD Probe Error; 30=From Proc RTD Probe Open; 31=From Proc RTD Probe Short; 32=From Proc RTD Probe Error; 33=Remote RTD Probe Open; 34=Remote RTD Probe Short; 35=Remote RTD Probe Error; 36=Analog Process In Too High; 37=Analog Process In Too Low; 38=Analog Process In Error; 39=Network Process In Too High; 40=Network Process In Too Low; 41=Network Proc In Heartbeat Lost; 42=Analog Setpoint Too High; 43=Analog Setpoint Too Low; 44=Analog Setpoint Error; 45=Network Setpoint High; 46=Network Setpoint Low; 47=Network Setpoint Heartbeat Lost; 48=Pressure Below Minimum; 49=Need More Press for this Temp; 50=From Process Press Sensor High; 51=From Process Press Sensor Low; 52=From Process Press Sensor Error; 53=To Process Press Sensor High; 54=To Process Press Sensor Low; 55=To Process Press Sensor Error; 56=Flowmeter Signal Too High; 57=Flowmeter Signal Too Low; 58=Flowmeter Signal Error; 59=Temperature Deviation High; 60=Temperature Deviation Low; 61=Network Heartbeat Lost; 62=Ramp/Soak Interrupted; 63=Autotune Startg Output Too High; 64=Autotune Process Response Slow; 65=Autotune Time Const Not Found; 66=Autotune Process Limit Exceeded. |  | Highest Priority Alarm
| TRUE | DISPLAY | n_HD_Alarm.Implemented | 42 | n_HD_Alarm.Implemented | Highest Priority Alarm | Off/On | Highest Priority Alarm
| TRUE | DISPLAY | n_HD_Alarm.Value |  | n_HD_Alarm.Value | Highest Priority Alarm. 1=IO Connection Failure; 2=IO Module Link Failure; 3=IO Module Hardware Mismatch; 4=IO Module Internal Fault; 5=IO Point Failure; 6=Power Supply Voltage Low; 7=Logic Supply Voltage Low; 8=Overtemperature Fault; 9=Heater Contactor Stuck Closed; 10=Temperature Over Limit; 11=Unbranded; 12=Factory Options Not Set; 13=Electric Power Fault; 14=Pump Contactor Stuck Closed; 15=Heater Contactor Stuck Open; 16=Pump Contactor Stuck Open; 17=System Pressure Too High; 18=Electrical Panel Too Hot; 19=Temperature Under Limit; 20=Brownout Occurred; 21=Temperature Over Setting; 22=Temperature Under Setting; 23=Low Pressure Shutdown; 24=Low Pressure Too Many Events; 25=Pump Overload Tripped; 26=Flowmeter Low Flow; 27=To Proc RTD Probe Open; 28=To Proc RTD Probe Short; 29=To Proc RTD Probe Error; 30=From Proc RTD Probe Open; 31=From Proc RTD Probe Short; 32=From Proc RTD Probe Error; 33=Remote RTD Probe Open; 34=Remote RTD Probe Short; 35=Remote RTD Probe Error; 36=Analog Process In Too High; 37=Analog Process In Too Low; 38=Analog Process In Error; 39=Network Process In Too High; 40=Network Process In Too Low; 41=Network Proc In Heartbeat Lost; 42=Analog Setpoint Too High; 43=Analog Setpoint Too Low; 44=Analog Setpoint Error; 45=Network Setpoint High; 46=Network Setpoint Low; 47=Network Setpoint Heartbeat Lost; 48=Pressure Below Minimum; 49=Need More Press for this Temp; 50=From Process Press Sensor High; 51=From Process Press Sensor Low; 52=From Process Press Sensor Error; 53=To Process Press Sensor High; 54=To Process Press Sensor Low; 55=To Process Press Sensor Error; 56=Flowmeter Signal Too High; 57=Flowmeter Signal Too Low; 58=Flowmeter Signal Error; 59=Temperature Deviation High; 60=Temperature Deviation Low; 61=Network Heartbeat Lost; 62=Ramp/Soak Interrupted; 63=Autotune Startg Output Too High; 64=Autotune Process Response Slow; 65=Autotune Time Const Not Found; 66=Autotune Process Limit Exceeded. | <enumeration> | Highest Priority Alarm
| TRUE | DISPLAY | n_HD_Alarm.Minimum |  | n_HD_Alarm.Minimum | Highest Priority Alarm | <enumeration> | Highest Priority Alarm
| TRUE | DISPLAY | n_HD_Alarm.Maximum |  | n_HD_Alarm.Maximum | Highest Priority Alarm | <enumeration> | Highest Priority Alarm
| TRUE | DISPLAY | n_HD_Alarm.Error |  | n_HD_Alarm.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration> | Highest Priority Alarm
| TRUE | DISPLAY | n_HD_Warning |  | n_HD_Warning | Highest Priority Warning. 1=Pump Overload Tripped; 2=Flowmeter Bad Flow; 3=To Proc RTD Probe Open (f/o); 4=To Proc RTD Probe Short (f/o); 5=To Proc RTD Probe Error (f/o); 6=From Proc RTD Probe Open (f/o); 7=From Proc RTD Probe Short (f/o); 8=From Proc RTD Probe Error (f/o); 9=Remote RTD Probe Open (f/o); 10=Remote RTD Probe Short (f/o); 11=Remote RTD Probe Error (f/o); 12=Analog Process In Too High (f/o); 13=Analog Process In Too Low (f/o); 14=Analog Process In Error (f/o); 15=Network Proc In Too High (f/o); 16=Network Proc In Too Low (f/o); 17=Network Proc In HB Lost (f/o); 18=Analog Setpoint Too High (f/o); 19=Analog Setpoint Too Low (f/o); 20=Analog Setpoint Error (f/o); 21=Network Setpoint Too High (f/o); 22=Network Setpoint Too Low (f/o); 23=Network Setpoint HB Lost (f/o); 24=Pressure Below Minimum; 25=Need More Press for this Temp; 26=Setpoint Too High for Pressure; 27=To Proc Pressure Sensor High; 28=To Proc Pressure Sensor Low; 29=To Proc Pressure Sensor Error; 30=To Proc RTD Probe Open; 31=To Proc RTD Probe Short; 32=To Proc RTD Probe Error; 33=From Proc RTD Probe Open; 34=From Proc RTD Probe Short; 35=From Proc RTD Probe Error; 36=Flowmeter Signal Too High; 37=Flowmeter Signal Too Low; 38=Flowmeter Signal Error; 39=Flash Memory Error; 40=Temperature Deviation High; 41=Temperature Deviation Low; 42=Network Heartbeat Lost; 43=Too Frequent Heat Cycles; 44=Work Out Heater Contactor; 45=Clock Not Set. |  | Highest Priority Warning
| TRUE | DISPLAY | n_HD_Warning.Implemented | 42 | n_HD_Warning.Implemented | Highest Priority Warning | Off/On | Highest Priority Warning
| TRUE | DISPLAY | n_HD_Warning.Value |  | n_HD_Warning.Value | Highest Priority Warning. 1=Pump Overload Tripped; 2=Flowmeter Bad Flow; 3=To Proc RTD Probe Open (f/o); 4=To Proc RTD Probe Short (f/o); 5=To Proc RTD Probe Error (f/o); 6=From Proc RTD Probe Open (f/o); 7=From Proc RTD Probe Short (f/o); 8=From Proc RTD Probe Error (f/o); 9=Remote RTD Probe Open (f/o); 10=Remote RTD Probe Short (f/o); 11=Remote RTD Probe Error (f/o); 12=Analog Process In Too High (f/o); 13=Analog Process In Too Low (f/o); 14=Analog Process In Error (f/o); 15=Network Proc In Too High (f/o); 16=Network Proc In Too Low (f/o); 17=Network Proc In HB Lost (f/o); 18=Analog Setpoint Too High (f/o); 19=Analog Setpoint Too Low (f/o); 20=Analog Setpoint Error (f/o); 21=Network Setpoint Too High (f/o); 22=Network Setpoint Too Low (f/o); 23=Network Setpoint HB Lost (f/o); 24=Pressure Below Minimum; 25=Need More Press for this Temp; 26=Setpoint Too High for Pressure; 27=To Proc Pressure Sensor High; 28=To Proc Pressure Sensor Low; 29=To Proc Pressure Sensor Error; 30=To Proc RTD Probe Open; 31=To Proc RTD Probe Short; 32=To Proc RTD Probe Error; 33=From Proc RTD Probe Open; 34=From Proc RTD Probe Short; 35=From Proc RTD Probe Error; 36=Flowmeter Signal Too High; 37=Flowmeter Signal Too Low; 38=Flowmeter Signal Error; 39=Flash Memory Error; 40=Temperature Deviation High; 41=Temperature Deviation Low; 42=Network Heartbeat Lost; 43=Too Frequent Heat Cycles; 44=Work Out Heater Contactor; 45=Clock Not Set. | <enumeration> | Highest Priority Warning
| TRUE | DISPLAY | n_HD_Warning.Minimum |  | n_HD_Warning.Minimum | Highest Priority Warning | <enumeration> | Highest Priority Warning
| TRUE | DISPLAY | n_HD_Warning.Maximum |  | n_HD_Warning.Maximum | Highest Priority Warning | <enumeration> | Highest Priority Warning
| TRUE | DISPLAY | n_HD_Warning.Error |  | n_HD_Warning.Error | Highest Priority Warning | <enumeration> | Highest Priority Warning
| TRUE | DISPLAY | b_HD_AlarmSilenceActive |  | b_HD_AlarmSilenceActive | This is the value shown on the touchscreen for high if the there is an alarm, but it has been silenced. 0=alarm not silenced; 1=alarm silenced.
| TRUE | DISPLAY | b_HD_AlarmSilenceActive.Implemented | 42 | b_HD_AlarmSilenceActive.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | b_HD_AlarmSilenceActive.Value | 42 | b_HD_AlarmSilenceActive.Value | This is the value shown on the touchscreen for high if the there is an alarm, but it has been silenced. 0=alarm not silenced; 1=alarm silenced. | Off/On
| TRUE | DISPLAY | b_HD_AlarmSilenceActive.Error |  | b_HD_AlarmSilenceActive.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_NPSHa |  | r_HD_NetPositiveSuctionHeadAvailable | This is the value shown on the touchscreen for net positive suction head available for pump. In units of psi.
| TRUE | DISPLAY | r_HD_NPSHa.Implemented | 42 | r_HD_NetPositiveSuctionHeadAvailable.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_NPSHa.Value | 13 | r_HD_NetPositiveSuctionHeadAvailable.Value | This is the value shown on the touchscreen for net positive suction head available for pump. In units of psi. | psi
| TRUE | DISPLAY | r_HD_NPSHa.Minimum | 13 | r_HD_NetPositiveSuctionHeadAvailable.Minimum | The minimum permitted value. | psi
| TRUE | DISPLAY | r_HD_NPSHa.Maximum | 13 | r_HD_NetPositiveSuctionHeadAvailable.Maximum | The maximum permitted value. | psi
| TRUE | DISPLAY | r_HD_NPSHa.Error |  | r_HD_NetPositiveSuctionHeadAvailable.Error | Describes if value is valid: 10=No Error; 3=Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_NPSHr |  | r_HD_NetPositiveSuctionHeadRequired | This is the value shown on the touchscreen for net positive suction head required by pump. In units of psi.
| TRUE | DISPLAY | r_HD_NPSHr.Implemented | 42 | r_HD_NetPositiveSuctionHeadRequired.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_NPSHr.Value | 13 | r_HD_NetPositiveSuctionHeadRequired.Value | This is the value shown on the touchscreen for net positive suction head required by pump. In units of psi. | psi
| TRUE | DISPLAY | r_HD_NPSHr.Minimum | 13 | r_HD_NetPositiveSuctionHeadRequired.Minimum | The minimum permitted value. | psi
| TRUE | DISPLAY | r_HD_NPSHr.Maximum | 13 | r_HD_NetPositiveSuctionHeadRequired.Maximum | The maximum permitted value. | psi
| TRUE | DISPLAY | r_HD_NPSHr.Error |  | r_HD_NetPositiveSuctionHeadRequired.Error | Describes if value is valid: 10=No Error; 3=Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_SystemPower_kW |  | r_HD_SystemPower_kW | This is the value shown on the touchscreen for current electrical power being consumed by the unit (according to component nameplate ratings). In units of kW.
| TRUE | DISPLAY | r_HD_SystemPower_kW.Implemented | 42 | r_HD_SystemPower_kW.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_SystemPower_kW.Value | 27 | r_HD_SystemPower_kW.Value | This is the value shown on the touchscreen for current electrical power being consumed by the unit (according to component nameplate ratings). In units of kW. | kW
| TRUE | DISPLAY | r_HD_SystemPower_kW.Minimum | 27 | r_HD_SystemPower_kW.Minimum | The minimum permitted value. | kW
| TRUE | DISPLAY | r_HD_SystemPower_kW.Maximum | 27 | r_HD_SystemPower_kW.Maximum | The maximum permitted value. | kW
| TRUE | DISPLAY | r_HD_SystemPower_kW.Error |  | r_HD_SystemPower_kW.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_SystemNominalPower_kW |  | r_HD_SystemNominalPower_kW | This is the value shown on the touchscreen for nominal electrical power being consumed by the unit if it was fully operational and heater was operating at 100%. In units of kW.
| TRUE | DISPLAY | r_HD_SystemNominalPower_kW.Implemented | 42 | r_HD_SystemNominalPower_kW.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_SystemNominalPower_kW.Value | 27 | r_HD_SystemNominalPower_kW.Value | This is the value shown on the touchscreen for nominal electrical power being consumed by the unit if it was fully operational and heater was operating at 100%. In units of kW. | kW
| TRUE | DISPLAY | r_HD_SystemNominalPower_kW.Minimum | 27 | r_HD_SystemNominalPower_kW.Minimum | The minimum permitted value. | kW
| TRUE | DISPLAY | r_HD_SystemNominalPower_kW.Maximum | 27 | r_HD_SystemNominalPower_kW.Maximum | The maximum permitted value. | kW
| TRUE | DISPLAY | r_HD_SystemNominalPower_kW.Error |  | r_HD_SystemNominalPower_kW.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | s_HD_OS_Version |  | s_HD_OperatingSystemVersion | This is the value shown on the touchscreen for firmware/os software revision level.
| TRUE | DISPLAY | s_HD_OS_Version.Implemented | 42 | s_HD_OperatingSystemVersion.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | s_HD_OS_Version.Value |  | s_HD_OperatingSystemVersion.Value | This is the value shown on the touchscreen for firmware/os software revision level. | N/A
| TRUE | DISPLAY | s_HD_OS_Version.Error |  | s_HD_OperatingSystemVersion.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | r_HD_SoftwareVersion |  | r_HD_SoftwareVersion | This is the value shown on the touchscreen for application software revision level.
| TRUE | DISPLAY | r_HD_SoftwareVersion.Implemented | 42 | r_HD_SoftwareVersion.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | r_HD_SoftwareVersion.Value |  | r_HD_SoftwareVersion.Value | This is the value shown on the touchscreen for application software revision level. | N/A
| TRUE | DISPLAY | r_HD_SoftwareVersion.Minimum |  | r_HD_SoftwareVersion.Minimum | The minimum permitted value. | N/A
| TRUE | DISPLAY | r_HD_SoftwareVersion.Maximum |  | r_HD_SoftwareVersion.Maximum | The maximum permitted value. | N/A
| TRUE | DISPLAY | r_HD_SoftwareVersion.Error |  | r_HD_SoftwareVersion.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorOps |  | u_HD_HEALTH_HeaterContactorOperations | This is the value shown on the touchscreen for operational cycle count for the electromechanical heater contactor. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorOps.Implemented | 42 | u_HD_HEALTH_HeaterContactorOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorOps.Value | 17 | u_HD_HEALTH_HeaterContactorOperations.Value | This is the value shown on the touchscreen for operational cycle count for the electromechanical heater contactor. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorOps.Minimum | 17 | u_HD_HEALTH_HeaterContactorOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorOps.Maximum | 17 | u_HD_HEALTH_HeaterContactorOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorOps.Error |  | u_HD_HEALTH_HeaterContactorOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_HeaterContrOps_NR | 17 | u_NET_HEALTH_HeaterContactorOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the electromechanical heater contactor. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorRt |  | u_HD_HEALTH_HeaterContactorRuntime | This is the value shown on the touchscreen for operational run time for the electromechanical heater contactor. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorRt.Implemented | 42 | u_HD_HEALTH_HeaterContactorRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorRt.Value | 10 | u_HD_HEALTH_HeaterContactorRuntime.Value | This is the value shown on the touchscreen for operational run time for the electromechanical heater contactor. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorRt.Minimum | 10 | u_HD_HEALTH_HeaterContactorRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorRt.Maximum | 10 | u_HD_HEALTH_HeaterContactorRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterContactorRt.Error |  | u_HD_HEALTH_HeaterContactorRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_HeaterContrRt_NR | 10 | u_NET_HEALTH_HeaterContactorRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the electromechanical heater contactor. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrOpenDly |  | u_HD_HEALTH_HeaterContactorOpenDelay | This is the value shown on the touchscreen for time delay between turning off the coil power to the heater electromechanical contactor & sensing the opening of the armature via the aux contacts on the heater electromechanical contactor. In units of milliseconds.
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrOpenDly.Implemented | 42 | u_HD_HEALTH_HeaterContactorOpenDelay.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrOpenDly.Value | 7 | u_HD_HEALTH_HeaterContactorOpenDelay.Value | This is the value shown on the touchscreen for time delay between turning off the coil power to the heater electromechanical contactor & sensing the opening of the armature via the aux contacts on the heater electromechanical contactor. In units of milliseconds. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrOpenDly.Minimum | 7 | u_HD_HEALTH_HeaterContactorOpenDelay.Minimum | The minimum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrOpenDly.Maximum | 7 | u_HD_HEALTH_HeaterContactorOpenDelay.Maximum | The maximum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrOpenDly.Error |  | u_HD_HEALTH_HeaterContactorOpenDelay.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrCloseDly |  | u_HD_HEALTH_HeaterContactorCloseDelay | This is the value shown on the touchscreen for time delay between turning on the coil power to the heater electromechanical contactor & sensing the closing of the armature via the aux contacts on the heater electromechanical contactor. In units of milliseconds.
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrCloseDly.Implemented | 42 | u_HD_HEALTH_HeaterContactorCloseDelay.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrCloseDly.Value | 7 | u_HD_HEALTH_HeaterContactorCloseDelay.Value | This is the value shown on the touchscreen for time delay between turning on the coil power to the heater electromechanical contactor & sensing the closing of the armature via the aux contacts on the heater electromechanical contactor. In units of milliseconds. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrCloseDly.Minimum | 7 | u_HD_HEALTH_HeaterContactorCloseDelay.Minimum | The minimum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrCloseDly.Maximum | 7 | u_HD_HEALTH_HeaterContactorCloseDelay.Maximum | The maximum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_HeaterContrCloseDly.Error |  | u_HD_HEALTH_HeaterContactorCloseDelay.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Ops |  | u_HD_HEALTH_HeaterSolidStateRelayOperations | This is the value shown on the touchscreen for operational cycle count for the solid state heater contactor. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Ops.Implemented | 42 | u_HD_HEALTH_HeaterSolidStateRelayOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Ops.Value | 17 | u_HD_HEALTH_HeaterSolidStateRelayOperations.Value | This is the value shown on the touchscreen for operational cycle count for the solid state heater contactor. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Ops.Minimum | 17 | u_HD_HEALTH_HeaterSolidStateRelayOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Ops.Maximum | 17 | u_HD_HEALTH_HeaterSolidStateRelayOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Ops.Error |  | u_HD_HEALTH_HeaterSolidStateRelayOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_HeaterSSR_Ops_NR | 17 | u_NET_HEALTH_HeaterSolidStateRelayOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the solid state heater contactor. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Rt |  | u_HD_HEALTH_HeaterSolidStateRelayRuntime | This is the value shown on the touchscreen for operational run time for the solid state heater contactor. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Rt.Implemented | 42 | u_HD_HEALTH_HeaterSolidStateRelayRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Rt.Value | 10 | u_HD_HEALTH_HeaterSolidStateRelayRuntime.Value | This is the value shown on the touchscreen for operational run time for the solid state heater contactor. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Rt.Minimum | 10 | u_HD_HEALTH_HeaterSolidStateRelayRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Rt.Maximum | 10 | u_HD_HEALTH_HeaterSolidStateRelayRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterSSR_Rt.Error |  | u_HD_HEALTH_HeaterSolidStateRelayRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_HeaterSSR_Rt_NR | 10 | u_NET_HEALTH_HeaterSolidStateRelayRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the solid state heater contactor. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterOps |  | u_HD_HEALTH_HeaterOperations | This is the value shown on the touchscreen for operational cycle count for the heater. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_HeaterOps.Implemented | 42 | u_HD_HEALTH_HeaterOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterOps.Value | 17 | u_HD_HEALTH_HeaterOperations.Value | This is the value shown on the touchscreen for operational cycle count for the heater. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterOps.Minimum | 17 | u_HD_HEALTH_HeaterOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterOps.Maximum | 17 | u_HD_HEALTH_HeaterOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterOps.Error |  | u_HD_HEALTH_HeaterOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_HeaterOps_NR | 17 | u_NET_HEALTH_HeaterOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the heater. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HeaterRt |  | u_HD_HEALTH_HeaterRuntime | This is the value shown on the touchscreen for operational run time for the heater. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_HeaterRt.Implemented | 42 | u_HD_HEALTH_HeaterRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeaterRt.Value | 10 | u_HD_HEALTH_HeaterRuntime.Value | This is the value shown on the touchscreen for operational run time for the heater. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterRt.Minimum | 10 | u_HD_HEALTH_HeaterRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterRt.Maximum | 10 | u_HD_HEALTH_HeaterRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_HeaterRt.Error |  | u_HD_HEALTH_HeaterRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_HeaterRt_NR | 10 | u_NET_HEALTH_HeaterRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the heater. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_ActuationRt |  | u_HD_HEALTH_CoolingValve_ActuationRuntime | This is the value shown on the touchscreen for operational run time for the cooling valve. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_CV_ActuationRt.Implemented | 42 | u_HD_HEALTH_CoolingValve_ActuationRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_CV_ActuationRt.Value | 10 | u_HD_HEALTH_CoolingValve_ActuationRuntime.Value | This is the value shown on the touchscreen for operational run time for the cooling valve. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_ActuationRt.Minimum | 10 | u_HD_HEALTH_CoolingValve_ActuationRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_ActuationRt.Maximum | 10 | u_HD_HEALTH_CoolingValve_ActuationRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_ActuationRt.Error |  | u_HD_HEALTH_CoolingValve_ActuationRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_CV_ActuationRt_NR | 10 | u_NET_HEALTH_CoolingValve_ActuationRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the cooling valve. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenOps |  | u_HD_HEALTH_CoolingValve_OpenOperations | This is the value shown on the touchscreen for operational cycle count for the cooling valve solenoid or floating valve open direction. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenOps.Implemented | 42 | u_HD_HEALTH_CoolingValve_OpenOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenOps.Value | 17 | u_HD_HEALTH_CoolingValve_OpenOperations.Value | This is the value shown on the touchscreen for operational cycle count for the cooling valve solenoid or floating valve open direction. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenOps.Minimum | 17 | u_HD_HEALTH_CoolingValve_OpenOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenOps.Maximum | 17 | u_HD_HEALTH_CoolingValve_OpenOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenOps.Error |  | u_HD_HEALTH_CoolingValve_OpenOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_CV_OpenOps_NR | 17 | u_NET_HEALTH_CoolingValve_OpenOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the cooling valve solenoid or floating valve open direction. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenRt |  | u_HD_HEALTH_CoolingValve_OpenRuntime | This is the value shown on the touchscreen for operational run time for the cooling valve solenoid or floating valve open direction. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenRt.Implemented | 42 | u_HD_HEALTH_CoolingValve_OpenRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenRt.Value | 10 | u_HD_HEALTH_CoolingValve_OpenRuntime.Value | This is the value shown on the touchscreen for operational run time for the cooling valve solenoid or floating valve open direction. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenRt.Minimum | 10 | u_HD_HEALTH_CoolingValve_OpenRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenRt.Maximum | 10 | u_HD_HEALTH_CoolingValve_OpenRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_OpenRt.Error |  | u_HD_HEALTH_CoolingValve_OpenRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_CV_OpenRt_NR | 10 | u_NET_HEALTH_CoolingValve_OpenRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the cooling valve solenoid or floating valve open direction. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseOps |  | u_HD_HEALTH_CoolingValve_CloseOperations | This is the value shown on the touchscreen for operational cycle count for the floating valve close direction. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseOps.Implemented | 42 | u_HD_HEALTH_CoolingValve_CloseOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseOps.Value | 17 | u_HD_HEALTH_CoolingValve_CloseOperations.Value | This is the value shown on the touchscreen for operational cycle count for the floating valve close direction. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseOps.Minimum | 17 | u_HD_HEALTH_CoolingValve_CloseOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseOps.Maximum | 17 | u_HD_HEALTH_CoolingValve_CloseOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseOps.Error |  | u_HD_HEALTH_CoolingValve_CloseOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_CV_CloseOps_NR | 17 | u_NET_HEALTH_CoolingValve_CloseOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the floating valve close direction. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseRt |  | u_HD_HEALTH_CoolingValve_CloseRuntime | This is the value shown on the touchscreen for operational run time for the floating valve close direction. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseRt.Implemented | 42 | u_HD_HEALTH_CoolingValve_CloseRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseRt.Value | 10 | u_HD_HEALTH_CoolingValve_CloseRuntime.Value | This is the value shown on the touchscreen for operational run time for the floating valve close direction. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseRt.Minimum | 10 | u_HD_HEALTH_CoolingValve_CloseRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseRt.Maximum | 10 | u_HD_HEALTH_CoolingValve_CloseRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_CV_CloseRt.Error |  | u_HD_HEALTH_CoolingValve_CloseRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_CV_CloseRt_NR | 10 | u_NET_HEALTH_CoolingValve_CloseRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the floating valve close direction. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpOps |  | u_HD_HEALTH_PumpOperations | This is the value shown on the touchscreen for operational cycle count for the pump. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_PumpOps.Implemented | 42 | u_HD_HEALTH_PumpOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PumpOps.Value | 17 | u_HD_HEALTH_PumpOperations.Value | This is the value shown on the touchscreen for operational cycle count for the pump. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpOps.Minimum | 17 | u_HD_HEALTH_PumpOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpOps.Maximum | 17 | u_HD_HEALTH_PumpOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpOps.Error |  | u_HD_HEALTH_PumpOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_PumpOps_NR | 17 | u_NET_HEALTH_PumpOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the pump. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpRt |  | u_HD_HEALTH_PumpRuntime | This is the value shown on the touchscreen for operational run time for the pump. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_PumpRt.Implemented | 42 | u_HD_HEALTH_PumpRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PumpRt.Value | 10 | u_HD_HEALTH_PumpRuntime.Value | This is the value shown on the touchscreen for operational run time for the pump. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpRt.Minimum | 10 | u_HD_HEALTH_PumpRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpRt.Maximum | 10 | u_HD_HEALTH_PumpRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpRt.Error |  | u_HD_HEALTH_PumpRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_PumpRt_NR | 10 | u_NET_HEALTH_PumpRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the pump. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorOps |  | u_HD_HEALTH_PumpContactorOperations | This is the value shown on the touchscreen for operational cycle count for the pump contactor. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorOps.Implemented | 42 | u_HD_HEALTH_PumpContactorOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorOps.Value | 17 | u_HD_HEALTH_PumpContactorOperations.Value | This is the value shown on the touchscreen for operational cycle count for the pump contactor. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorOps.Minimum | 17 | u_HD_HEALTH_PumpContactorOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorOps.Maximum | 17 | u_HD_HEALTH_PumpContactorOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorOps.Error |  | u_HD_HEALTH_PumpContactorOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_PumpContactorOps_NR | 17 | u_NET_HEALTH_PumpContactorOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the pump contactor. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorRt |  | u_HD_HEALTH_PumpContactorRuntime | This is the value shown on the touchscreen for operational run time for the pump contactor. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorRt.Implemented | 42 | u_HD_HEALTH_PumpContactorRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorRt.Value | 10 | u_HD_HEALTH_PumpContactorRuntime.Value | This is the value shown on the touchscreen for operational run time for the pump contactor. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorRt.Minimum | 10 | u_HD_HEALTH_PumpContactorRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorRt.Maximum | 10 | u_HD_HEALTH_PumpContactorRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpContactorRt.Error |  | u_HD_HEALTH_PumpContactorRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_PumpContactorRt_NR | 10 | u_NET_HEALTH_PumpContactorRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the pump contactor. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_PumpContrOpenDly |  | u_HD_HEALTH_PumpContactorOpenDelay | This is the value shown on the touchscreen for time delay between turning off the coil power to the pump electromechanical contactor & sensing the opening of the armature via the aux contacts on the pump electromechanical contactor. In units of milliseconds.
| TRUE | HEALTH | u_HD_HEALTH_PumpContrOpenDly.Implemented | 42 | u_HD_HEALTH_PumpContactorOpenDelay.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PumpContrOpenDly.Value | 7 | u_HD_HEALTH_PumpContactorOpenDelay.Value | This is the value shown on the touchscreen for time delay between turning off the coil power to the pump electromechanical contactor & sensing the opening of the armature via the aux contacts on the pump electromechanical contactor. In units of milliseconds. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_PumpContrOpenDly.Minimum | 7 | u_HD_HEALTH_PumpContactorOpenDelay.Minimum | The minimum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_PumpContrOpenDly.Maximum | 7 | u_HD_HEALTH_PumpContactorOpenDelay.Maximum | The maximum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_PumpContrOpenDly.Error |  | u_HD_HEALTH_PumpContactorOpenDelay.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_PumpContrCloseDly |  | u_HD_HEALTH_PumpContactorCloseDelay | This is the value shown on the touchscreen for time delay between turning on the coil power on the pump electromechanical contactor & sensing the closing of the armature via the aux contacts on the pump electromechanical contactor. In units of milliseconds.
| TRUE | HEALTH | u_HD_HEALTH_PumpContrCloseDly.Implemented | 42 | u_HD_HEALTH_PumpContactorCloseDelay.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PumpContrCloseDly.Value | 7 | u_HD_HEALTH_PumpContactorCloseDelay.Value | This is the value shown on the touchscreen for time delay between turning on the coil power on the pump electromechanical contactor & sensing the closing of the armature via the aux contacts on the pump electromechanical contactor. In units of milliseconds. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_PumpContrCloseDly.Minimum | 7 | u_HD_HEALTH_PumpContactorCloseDelay.Minimum | The minimum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_PumpContrCloseDly.Maximum | 7 | u_HD_HEALTH_PumpContactorCloseDelay.Maximum | The maximum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_PumpContrCloseDly.Error |  | u_HD_HEALTH_PumpContactorCloseDelay.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_PresSwOps |  | u_HD_HEALTH_PressureSwitchOperations | This is the value shown on the touchscreen for operational cycle count for the pressure switch. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_PresSwOps.Implemented | 42 | u_HD_HEALTH_PressureSwitchOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PresSwOps.Value | 17 | u_HD_HEALTH_PressureSwitchOperations.Value | This is the value shown on the touchscreen for operational cycle count for the pressure switch. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PresSwOps.Minimum | 17 | u_HD_HEALTH_PressureSwitchOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PresSwOps.Maximum | 17 | u_HD_HEALTH_PressureSwitchOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PresSwOps.Error |  | u_HD_HEALTH_PressureSwitchOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_PresSwOps_NR | 17 | u_NET_HEALTH_PressureSwitchOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the pressure switch. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_MoldPurgeOps |  | u_HD_HEALTH_MoldPurgeOperations | This is the value shown on the touchscreen for operational cycle count for the mold purge solenoid valves. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_MoldPurgeOps.Implemented | 42 | u_HD_HEALTH_MoldPurgeOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_MoldPurgeOps.Value | 17 | u_HD_HEALTH_MoldPurgeOperations.Value | This is the value shown on the touchscreen for operational cycle count for the mold purge solenoid valves. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_MoldPurgeOps.Minimum | 17 | u_HD_HEALTH_MoldPurgeOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_MoldPurgeOps.Maximum | 17 | u_HD_HEALTH_MoldPurgeOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_MoldPurgeOps.Error |  | u_HD_HEALTH_MoldPurgeOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_MoldPurgeOps_NR | 17 | u_NET_HEALTH_MoldPurgeOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the mold purge solenoid valves. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_VentSolOps |  | u_HD_HEALTH_VentSolenoidOperations | This is the value shown on the touchscreen for operational cycle count for the vent solenoid. (not shown in HMI.) In unit of operations.
| TRUE | HEALTH | u_HD_HEALTH_VentSolOps.Implemented | 42 | u_HD_HEALTH_VentSolenoidOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_VentSolOps.Value | 17 | u_HD_HEALTH_VentSolenoidOperations.Value | This is the value shown on the touchscreen for operational cycle count for the vent solenoid. (not shown in HMI.) In unit of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_VentSolOps.Minimum | 17 | u_HD_HEALTH_VentSolenoidOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_VentSolOps.Maximum | 17 | u_HD_HEALTH_VentSolenoidOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_VentSolOps.Error |  | u_HD_HEALTH_VentSolenoidOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_VentSolOps_NR | 17 | u_NET_HEALTH_VentSolenoidOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the vent solenoid. (not shown in HMI.) In unit of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpOL_Ops |  | u_HD_HEALTH_PumpOverload_Operations | This is the value shown on the touchscreen for count of number of trips of the pump overload. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_PumpOL_Ops.Implemented | 42 | u_HD_HEALTH_PumpOverload_Operations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PumpOL_Ops.Value | 17 | u_HD_HEALTH_PumpOverload_Operations.Value | This is the value shown on the touchscreen for count of number of trips of the pump overload. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpOL_Ops.Minimum | 17 | u_HD_HEALTH_PumpOverload_Operations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpOL_Ops.Maximum | 17 | u_HD_HEALTH_PumpOverload_Operations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PumpOL_Ops.Error |  | u_HD_HEALTH_PumpOverload_Operations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_PumpOL_Ops_NR | 17 | u_NET_HEALTH_PumpOverload_OperationsNonResettable | This is the value shown on the touchscreen for non-resettable count of number of trips of the pump overload. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_AlarmOps |  | u_HD_HEALTH_AlarmOperations | This is the value shown on the touchscreen for count for number of alarms. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_AlarmOps.Implemented | 42 | u_HD_HEALTH_AlarmOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_AlarmOps.Value | 17 | u_HD_HEALTH_AlarmOperations.Value | This is the value shown on the touchscreen for count for number of alarms. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_AlarmOps.Minimum | 17 | u_HD_HEALTH_AlarmOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_AlarmOps.Maximum | 17 | u_HD_HEALTH_AlarmOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_AlarmOps.Error |  | u_HD_HEALTH_AlarmOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_AlarmOps_NR | 17 | u_NET_HEALTH_AlarmOperationsNonResettable | This is the value shown on the touchscreen for non-resettable count for number of alarms. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HighTempOps |  | u_HD_HEALTH_HighTemperatureOperations | This is the value shown on the touchscreen for count for number of high-temperature alarms. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_HighTempOps.Implemented | 42 | u_HD_HEALTH_HighTemperatureOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HighTempOps.Value | 17 | u_HD_HEALTH_HighTemperatureOperations.Value | This is the value shown on the touchscreen for count for number of high-temperature alarms. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_HighTempOps.Minimum | 17 | u_HD_HEALTH_HighTemperatureOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HighTempOps.Maximum | 17 | u_HD_HEALTH_HighTemperatureOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_HighTempOps.Error |  | u_HD_HEALTH_HighTemperatureOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_HighTempOps_NR | 17 | u_NET_HEALTH_HighTemperatureOperationsNonResettable | This is the value shown on the touchscreen for non-resettable count for number of high-temperature alarms. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PhaseMonitorOps |  | u_HD_HEALTH_PhaseMonitorOperations | This is the value shown on the touchscreen for count for number of phase monitor alarms. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_PhaseMonitorOps.Implemented | 42 | u_HD_HEALTH_PhaseMonitorOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_PhaseMonitorOps.Value | 17 | u_HD_HEALTH_PhaseMonitorOperations.Value | This is the value shown on the touchscreen for count for number of phase monitor alarms. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_PhaseMonitorOps.Minimum | 17 | u_HD_HEALTH_PhaseMonitorOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PhaseMonitorOps.Maximum | 17 | u_HD_HEALTH_PhaseMonitorOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_PhaseMonitorOps.Error |  | u_HD_HEALTH_PhaseMonitorOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_PhaseMonitorOps_NR | 17 | u_NET_HEALTH_PhaseMonitorOperationsNonResettable | This is the value shown on the touchscreen for non-resettable count for number of phase monitor alarms. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_CoolingLTA |  | u_HD_HEALTH_CoolingLongTermAverage | This is the value shown on the touchscreen for long term cooling capacity utilization. In units of %.
| TRUE | HEALTH | u_HD_HEALTH_CoolingLTA.Implemented | 42 | u_HD_HEALTH_CoolingLongTermAverage.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_CoolingLTA.Value | 11 | u_HD_HEALTH_CoolingLongTermAverage.Value | This is the value shown on the touchscreen for long term cooling capacity utilization. In units of %. | %
| TRUE | HEALTH | u_HD_HEALTH_CoolingLTA.Minimum | 11 | u_HD_HEALTH_CoolingLongTermAverage.Minimum | The minimum permitted value. | %
| TRUE | HEALTH | u_HD_HEALTH_CoolingLTA.Maximum | 11 | u_HD_HEALTH_CoolingLongTermAverage.Maximum | The maximum permitted value. | %
| TRUE | HEALTH | u_HD_HEALTH_CoolingLTA.Error |  | u_HD_HEALTH_CoolingLongTermAverage.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_HeatingLTA |  | u_HD_HEALTH_HeatingLongTermAverage | This is the value shown on the touchscreen for long term heating capacity utilization. In units of %.
| TRUE | HEALTH | u_HD_HEALTH_HeatingLTA.Implemented | 42 | u_HD_HEALTH_HeatingLongTermAverage.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_HeatingLTA.Value | 11 | u_HD_HEALTH_HeatingLongTermAverage.Value | This is the value shown on the touchscreen for long term heating capacity utilization. In units of %. | %
| TRUE | HEALTH | u_HD_HEALTH_HeatingLTA.Minimum | 11 | u_HD_HEALTH_HeatingLongTermAverage.Minimum | The minimum permitted value. | %
| TRUE | HEALTH | u_HD_HEALTH_HeatingLTA.Maximum | 11 | u_HD_HEALTH_HeatingLongTermAverage.Maximum | The maximum permitted value. | %
| TRUE | HEALTH | u_HD_HEALTH_HeatingLTA.Error |  | u_HD_HEALTH_HeatingLongTermAverage.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_LastAlarmDuration |  | u_HD_HEALTH_LastAlarmDuration | This is the value shown on the touchscreen for last alarm duration. In units of seconds.
| TRUE | HEALTH | u_HD_HEALTH_LastAlarmDuration.Implemented | 42 | u_HD_HEALTH_LastAlarmDuration.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_LastAlarmDuration.Value | 8 | u_HD_HEALTH_LastAlarmDuration.Value | This is the value shown on the touchscreen for last alarm duration. In units of seconds. | seconds
| TRUE | HEALTH | u_HD_HEALTH_LastAlarmDuration.Minimum | 8 | u_HD_HEALTH_LastAlarmDuration.Minimum | The minimum permitted value. | seconds
| TRUE | HEALTH | u_HD_HEALTH_LastAlarmDuration.Maximum | 8 | u_HD_HEALTH_LastAlarmDuration.Maximum | The maximum permitted value. | seconds
| TRUE | HEALTH | u_HD_HEALTH_LastAlarmDuration.Error |  | u_HD_HEALTH_LastAlarmDuration.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_LowPressure |  | u_HD_HEALTH_LowPressure | This is the value shown on the touchscreen for count of low pressure pause states.
| TRUE | HEALTH | u_HD_HEALTH_LowPressure.Implemented | 42 | u_HD_HEALTH_LowPressure.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_LowPressure.Value | 17 | u_HD_HEALTH_LowPressure.Value | This is the value shown on the touchscreen for count of low pressure pause states. | operations
| TRUE | HEALTH | u_HD_HEALTH_LowPressure.Minimum | 17 | u_HD_HEALTH_LowPressure.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_LowPressure.Maximum | 17 | u_HD_HEALTH_LowPressure.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_LowPressure.Error |  | u_HD_HEALTH_LowPressure.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_LowPressure_NR | 17 | u_NET_HEALTH_LowPressureNonResettable | This is the value shown on the touchscreen for count of low pressure pause states. | operations
| FALSE | HEALTH | u_HD_HEALTH_MemWrites_x100000 |  | u_HD_HEALTH_MemoryWrites_x100000 | Not currently implemented.
| FALSE | HEALTH | u_HD_HEALTH_MemWrites_x100000.Implemented | 42 | u_HD_HEALTH_MemoryWrites_x100000.Implemented | Not currently implemented. | Off/On
| FALSE | HEALTH | u_HD_HEALTH_MemWrites_x100000.Value | 17 | u_HD_HEALTH_MemoryWrites_x100000.Value | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_MemWrites_x100000.Minimum | 17 | u_HD_HEALTH_MemoryWrites_x100000.Minimum | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_MemWrites_x100000.Maximum | 17 | u_HD_HEALTH_MemoryWrites_x100000.Maximum | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_MemWrites_x100000.Error |  | u_HD_HEALTH_MemoryWrites_x100000.Error | Not currently implemented. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_LoopTime_ms |  | u_HD_HEALTH_LoopTime_ms | This is the value shown on the touchscreen for last logic execution loop time. In units of milliseconds.
| TRUE | HEALTH | u_HD_HEALTH_LoopTime_ms.Implemented | 42 | u_HD_HEALTH_LoopTime_ms.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_LoopTime_ms.Value | 7 | u_HD_HEALTH_LoopTime_ms.Value | This is the value shown on the touchscreen for last logic execution loop time. In units of milliseconds. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_LoopTime_ms.Minimum | 7 | u_HD_HEALTH_LoopTime_ms.Minimum | The minimum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_LoopTime_ms.Maximum | 7 | u_HD_HEALTH_LoopTime_ms.Maximum | The maximum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_LoopTime_ms.Error |  | u_HD_HEALTH_LoopTime_ms.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_LoopTimeMax |  | u_HD_HEALTH_LoopTimeMaximum | This is the value shown on the touchscreen for maximum logic execution loop time. In units of milliseconds.
| TRUE | HEALTH | u_HD_HEALTH_LoopTimeMax.Implemented | 42 | u_HD_HEALTH_LoopTimeMaximum.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_LoopTimeMax.Value | 7 | u_HD_HEALTH_LoopTimeMaximum.Value | This is the value shown on the touchscreen for maximum logic execution loop time. In units of milliseconds. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_LoopTimeMax.Minimum | 7 | u_HD_HEALTH_LoopTimeMaximum.Minimum | The minimum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_LoopTimeMax.Maximum | 7 | u_HD_HEALTH_LoopTimeMaximum.Maximumimum | The maximum permitted value. | milliseconds
| TRUE | HEALTH | u_HD_HEALTH_LoopTimeMax.Error |  | u_HD_HEALTH_LoopTimeMaximum.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchOps |  | u_HD_HEALTH_FlowswitchOperations | This is the value shown on the touchscreen for operational cycle count for the flow switch. In units of operations.
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchOps.Implemented | 42 | u_HD_HEALTH_FlowswitchOperations.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchOps.Value | 17 | u_HD_HEALTH_FlowswitchOperations.Value | This is the value shown on the touchscreen for operational cycle count for the flow switch. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchOps.Minimum | 17 | u_HD_HEALTH_FlowswitchOperations.Minimum | The minimum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchOps.Maximum | 17 | u_HD_HEALTH_FlowswitchOperations.Maximum | The maximum permitted value. | operations
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchOps.Error |  | u_HD_HEALTH_FlowswitchOperations.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_FlowswitchOps_NR | 17 | u_NET_HEALTH_FlowswitchOperationsNonResettable | This is the value shown on the touchscreen for non-resettable operational cycle count for the flow switch. In units of operations. | operations
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchRt |  | u_HD_HEALTH_FlowswitchRuntime | This is the value shown on the touchscreen for operational run time for the flow switch. In units of hours.
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchRt.Implemented | 42 | u_HD_HEALTH_FlowswitchRuntime.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchRt.Value | 10 | u_HD_HEALTH_FlowswitchRuntime.Value | This is the value shown on the touchscreen for operational run time for the flow switch. In units of hours. | hours
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchRt.Minimum | 10 | u_HD_HEALTH_FlowswitchRuntime.Minimum | The minimum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchRt.Maximum | 10 | u_HD_HEALTH_FlowswitchRuntime.Maximum | The maximum permitted value. | hours
| TRUE | HEALTH | u_HD_HEALTH_FlowswitchRt.Error |  | u_HD_HEALTH_FlowswitchRuntime.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | HEALTH | u_NET_HEALTH_FlowswitchRt_NR | 10 | u_NET_HEALTH_FlowswitchRuntimeNonResettable | This is the value shown on the touchscreen for non-resettable operational run time for the flow switch. In units of hours. | hours
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolOps |  | u_HD_HEALTH_CrashCoolOperations | Not currently implemented.
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolOps.Implemented | 42 | u_HD_HEALTH_CrashCoolOperations.Implemented | Not currently implemented. | Off/On
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolOps.Value | 17 | u_HD_HEALTH_CrashCoolOperations.Value | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolOps.Minimum | 17 | u_HD_HEALTH_CrashCoolOperations.Minimum | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolOps.Maximum | 17 | u_HD_HEALTH_CrashCoolOperations.Maximum | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolOps.Error |  | u_HD_HEALTH_CrashCoolOperations.Error | Not currently implemented. | <enumeration>
| FALSE | HEALTH | u_NET_HEALTH_CrashCoolOps_NR | 17 | u_NET_HEALTH_CrashCoolOperationsNonResettable | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolRt |  | u_HD_HEALTH_CrashCoolRuntime | Not currently implemented.
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolRt.Implemented | 42 | u_HD_HEALTH_CrashCoolRuntime.Implemented | Not currently implemented. | Off/On
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolRt.Value | 10 | u_HD_HEALTH_CrashCoolRuntime.Value | Not currently implemented. | hours
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolRt.Minimum | 10 | u_HD_HEALTH_CrashCoolRuntime.Minimum | Not currently implemented. | hours
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolRt.Maximum | 10 | u_HD_HEALTH_CrashCoolRuntime.Maximum | Not currently implemented. | hours
| FALSE | HEALTH | u_HD_HEALTH_CrashCoolRt.Error |  | u_HD_HEALTH_CrashCoolRuntime.Error | Not currently implemented. | <enumeration>
| FALSE | HEALTH | u_NET_HEALTH_CrashCoolRt_NR | 10 | u_NET_HEALTH_CrashCoolRuntimeNonResettable | Not currently implemented. | hours
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveOps |  | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveOperations | Not currently implemented.
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveOps.Implemented | 42 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveOperations.Implemented | Not currently implemented. | Off/On
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveOps.Value | 17 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveOperations.Value | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveOps.Minimum | 17 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveOperations.Minimum | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveOps.Maximum | 17 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveOperations.Maximum | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveOps.Error |  | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveOperations.Error | Not currently implemented. | <enumeration>
| FALSE | HEALTH | u_NET_HEALTH_CCSS_FillVlvOps_NR | 17 | u_NET_HEALTH_ClosedCircuitSeperateSource_FillValveOperationsNonResettable | Not currently implemented. | operations
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveRt |  | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveRuntime | Not currently implemented.
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveRt.Implemented | 42 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveRuntime.Implemented | Not currently implemented. | Off/On
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveRt.Value | 10 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveRuntime.Value | Not currently implemented. | hours
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveRt.Minimum | 10 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveRuntime.Minimum | Not currently implemented. | hours
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveRt.Maximum | 10 | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveRuntime.Maximum | Not currently implemented. | hours
| FALSE | HEALTH | u_HD_HEALTH_CCSS_FillValveRt.Error |  | u_HD_HEALTH_ClosedCircuitSeperateSource_FillValveRuntime.Error | Not currently implemented. | <enumeration>
| FALSE | HEALTH | u_NET_HEALTH_CCSS_FillVlvRt_NR | 10 | u_NET_HEALTH_ClosedCircuitSeperateSource_FillValveRuntimeNonResettable | Not currently implemented. | hours
| TRUE | HEALTH | r_HD_HEALTH_ElecEnclosureTemp |  | r_HD_HEALTH_ElectricalEnclosureTemperature | This is the value shown on the touchscreen for temperature of the electrical enclosure. In units of °C.
| TRUE | HEALTH | r_HD_HEALTH_ElecEnclosureTemp.Implemented | 42 | r_HD_HEALTH_ElectricalEnclosureTemperature.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | HEALTH | r_HD_HEALTH_ElecEnclosureTemp.Value | 2 | r_HD_HEALTH_ElectricalEnclosureTemperature.Value | This is the value shown on the touchscreen for temperature of the electrical enclosure. In units of °C. | °C
| TRUE | HEALTH | r_HD_HEALTH_ElecEnclosureTemp.Minimum | 2 | r_HD_HEALTH_ElectricalEnclosureTemperature.Minimum | The minimum permitted value. | °C
| TRUE | HEALTH | r_HD_HEALTH_ElecEnclosureTemp.Maximum | 2 | r_HD_HEALTH_ElectricalEnclosureTemperature.Maximum | The maximum permitted value. | °C
| TRUE | HEALTH | r_HD_HEALTH_ElecEnclosureTemp.Error |  | r_HD_HEALTH_ElectricalEnclosureTemperature.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
| TRUE | DISPLAY | n_HD_ScreensaverColor |  | n_HD_ScreensaverColor | The color of the screensaver. 0=Unknown; 1=Stopped (Black background, white text); 2=Running (Green background, white text); 3=Non-Shutdown Alarm (Warning) (Orange background, black text); 4=Shutdown Alarm (Red background, black text)
| TRUE | DISPLAY | n_HD_ScreensaverColor.Implemented | 42 | n_HD_ScreensaverColor.Implemented | This value is only valid on the unit if this bit is TRUE. | Off/On
| TRUE | DISPLAY | n_HD_ScreensaverColor.Value |  | n_HD_ScreensaverColor.Value | The color of the screensaver. 0=Unknown; 1=Stopped (Black background, white text); 2=Running (Green background, white text); 3=Non-Shutdown Alarm (Warning) (Orange background, black text); 4=Shutdown Alarm (Red background, black text) | <enumeration>
| TRUE | DISPLAY | n_HD_ScreensaverColor.Minimum |  | n_HD_ScreensaverColor.Minimum | The minimum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_ScreensaverColor.Maximum |  | n_HD_ScreensaverColor.Maximum | The maximum permitted value. | <enumeration>
| TRUE | DISPLAY | n_HD_ScreensaverColor.Error |  | n_HD_ScreensaverColor.Error | Describes if value is valid: 10=No Error; 0=Error. | <enumeration>
Power Consumption
| TRUE | POWER | r_PumpNominalPower_W | 26 | r_PumpNominalPower_W | The electrical nameplate power the pump will consume, when running. In units of watts (W). | W
| TRUE | POWER | r_HeaterNominalPower_W | 26 | r_HeaterNominalPower_W | The electrical nameplate power the heater will consume, when running at 100%. In units of watts (W). | W
| TRUE | POWER | r_ControlNominalPower_W | 26 | r_ControlNominalPower_W | The electrical power the internal controls will consume. In units of watts (W). | W
| TRUE | POWER | r_SystemNominalPower_kW | 27 | r_SystemNominalPower_kW | The total electrical nameplate power the unit will consume when fully operational and heating at 100%. In units of kilowatts (kW). | kW
| TRUE | POWER | r_PumpPower_W | 26 | r_PumpPower_W | The electrical power the pump is currently consuming (based on nameplate, if running). In units of watts (W). | W
| TRUE | POWER | r_HeaterPower_W | 26 | r_HeaterPower_W | The electrical power the heater is currently consuming (based on nameplate if running at 100%. In units of watts (W). | W
| TRUE | POWER | r_ControlPower_W | 26 | r_ControlPower_W | The electrical power the internal controls are consuming. In units of watts (W). | W
| TRUE | POWER | r_SystemPower_kW | 27 | r_SystemPower_kW | The total electrical power the unit is currently consuming (based on nameplate ratings of components). In units of kilowatts (kW). | kW
Date/Time
| TRUE | DATE_TIME | st_CurrentLocalDateTime |  | st_CurrentLocalDateTime | The current date time in the onboard Real-Time-Clock ("RTC"). |  | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.Year |  | st_CurrentLocalDateTime.Year | The current year, as reported by the onboard Real Time Clock. 4-digit year format. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.Month |  | st_CurrentLocalDateTime.Month | The current month, as reported by the onboard Real Time Clock. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.Day |  | st_CurrentLocalDateTime.Day | The current day, as reported by the onboard Real Time Clock. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.Hour |  | st_CurrentLocalDateTime.Hour | The current hour, as reported by the onboard Real Time Clock. 24-hour format. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.Minute |  | st_CurrentLocalDateTime.Minute | The current minute, as reported by the onboard Real Time Clock. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.Second |  | st_CurrentLocalDateTime.Second | The current second, as reported by the onboard Real Time Clock. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.DayOfWeek |  | st_CurrentLocalDateTime.DayOfWeek | The current second, as reported by the onboard Real Time Clock. Enumeration of 1 through 7, 1=Monday. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.TimezoneOffset |  | st_CurrentLocalDateTime.TimezoneOffset | The time zone offset, as reported by the onboard Real Time Clock. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.MsSincePowerup |  | st_CurrentLocalDateTime.MsSincePowerup | The number of milliseconds since powerup. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_CurrentLocalDateTime.DstActive |  | st_CurrentLocalDateTime.DstActive | Whether or not Daylight Savings Time ("DST") is active, as reported by the onboard Real Time Clock. | N/A | See details on Modbus_Status sheet.
| TRUE | DATE_TIME | st_NET_DateTimeToSet |  | st_NET_DateTimeToSet | Information used to load into the RTC when "Setting" times into the real time clock.
| TRUE | DATE_TIME | st_NET_DateTimeToSet.Execute |  | st_NET_DateTimeToSet.Execute | Set this bit high to load "To Set" times into the real time clock. | N/A
| TRUE | DATE_TIME | st_NET_DateTimeToSet.Year |  | st_NET_DateTimeToSet.Year | Time to set: The year to set in the onboard Real Time Clock. 4-digit year format. | N/A
| TRUE | DATE_TIME | st_NET_DateTimeToSet.Month |  | st_NET_DateTimeToSet.Month | Time to set: The month to set in the onboard Real Time Clock. | N/A
| TRUE | DATE_TIME | st_NET_DateTimeToSet.Day |  | st_NET_DateTimeToSet.Day | Time to set: The day to set in the onboard Real Time Clock. | N/A
| TRUE | DATE_TIME | st_NET_DateTimeToSet.Hour |  | st_NET_DateTimeToSet.Hour | Time to set: The hour to set in the onboard Real Time Clock. 24-hour format. | N/A
| TRUE | DATE_TIME | st_NET_DateTimeToSet.Minute |  | st_NET_DateTimeToSet.Minute | Time to set: The minute to set in the onboard Real Time Clock. | N/A
| TRUE | DATE_TIME | st_NET_DateTimeToSet.Second |  | st_NET_DateTimeToSet.Second | Time to set: The second to set in the onboard Real Time Clock. | N/A
| TRUE | DATE_TIME | n_NET_RTC_SetClockCount | 43 | n_NET_RTC_SetClockCount | Number of times the RTC has been set on the unit. | counts
| TRUE | ALM_WRN_LIST | st_EM_ActiveErrorDataType |  | st_EM_ActiveErrorDataType | Full list of all active warnings and alarms, including descriptions, listed in array of order of severity. Highest urgency=highest severity number. 667-1000=Alarms, 334-666=Warnings, 1-333=Informational.

## Euromap
EUROMAP 82.1 DEFINITION
--References not only Euromap 82.1, but also Euromap 83.
| ENABLED | BROWSENAME | DATATYPE | TYPE DEFINITION | DESCRIPTION | UNITS | MANDATORY / OPTIONAL | READ-ONLY / READ/WRITE | NOTES | LINKED TAG
6: TCD_lnterfaceType
| YES | Identification | ---Object--- | IdentificationType | Euromap 83: The IdentificationType represents general information about a machine. The information is fixed by the manufacturer and not changeable by the user. | --- | Mandatory | Read-Only | Table 6, defined in Euromap 83, Table 125 see further down.
| YES | TCDSpecification | ---Object--- | TCDSpecificationType | Represents the basic specification of a TCD temperature control device with its subcomponents | --- | Mandatory | Read-Only | Table 6, see type definition further down in Table 7.
| YES | MachineConfiguration | ---Object--- | MachineConfigurationType | Euromap 83: This OPC UA ObjectType represents the current configuration of a machine. | --- | Mandatory | Read-Only | Table 6, defined in Euromap 83, Table 27 see further down.
| YES | Operation | ---Object--- | OperationType | Contains components which are necessary to operate the TCD. | --- | Mandatory | Read-Only | Table 6, see type definition further down in Table 8.
| YES | DeviceZone | ---Object--- | DeviceZoneType | Represents the functional main component of a TCD. | --- | Mandatory | Read-Only | Table 6, see type definition further down in Table 12.
| NO | DisplayLanguage | LocaleId | PropertyType | Allows the client can set the desired language on the user interface at the TCD. If the peripheral device does not support the configured language, it can keep the previous setting or use English as the default. | --- | Optional | RW | Table 6
| YES | TCDHelpOffNormalAlarmType | ---ObjectType--- | TCDHelpOffNormalAlarmType | The value of DeviceMappingNumber corresponds to the value given in the instance of the OperationType for assigning the alarm to a device. | --- | --- | --- | Table 6, see type definition further down in Table 26.
7: TCDSpecificationType (part of TCD_lnterfaceType)
| YES | MaxTemperature | Int32 | AnalogItemType | Defines the maximum working temperature of the TCD | °C | Mandatory | Read-Only | Table 7, element in Table 6 above. | n_EM_MaxTemperature
| YES | PowerValue | Double | AnalogItemType | Power value, defines the heating capacity of the TCD with the rated voltage | kW | Mandatory | Read-Only | Table 7, element in Table 6 above. | r_EM_PowerValue
| YES | ConnectedLoad | Double | AnalogItemType | Connected load, defines the connections of the TCD (pump performance, heating capacity and performance of the remaining components). | kW | Mandatory | Read-Only | Table 7, element in Table 6 above. | r_EM_ConnectedLoad
| YES | NominalFlowRate | Double | AnalogItemType | Nominal flow rate, defines the maximum achievable flow rate of the TCD. | gal/min | Mandatory | Read-Only | Table 7, element in Table 6 above. | r_EM_NominalFlowRate
| NO | CoolingCapacity | UInt32 | AnalogItemType | Power value for cooling, defines the power value for cooling at temperature difference of 60 K between cooling water and heat transfer medium | kW | Optional | Read-Only | Table 7, element in Table 6 above.
| YES | DeviceZoneId | String | Property | As written in 4.1, for a TCD with several device zones, there shall be several instances of TCD_InterfaceType with one object DeviceZone each. In this case, the DeviceZoneId shall be used to identify the different device zones. | --- | Optional | Read-Only | Table 7, element in Table 6 above. | s_EM_DeviceZoneId
8: OperationType (part of TCD_lnterfaceType)
| YES | DeviceMappingNumber | UInt32 | PropertyType | Unique identifier/address/number for devices of the same DeviceType within a local network. Several peripheral devices of the same DeviceType can be connected to a machine. In most applications, the machine must map the connected peripheral devices to internal logical devices and zones in a fixed configuration (e.g. hot runner systems | --- | Mandatory | Read/Write | Table 8, element in Table 6 above. | n_EM_DeviceMappingNumber
according to the wiring or temperature control devices according to the tubing). The mapping shall be stable after reconnecting the devices and is therefore not possible via IP addresses, which can be assigned dynamically via DHCP. DeviceMappingNumber sets the mapping order of peripheral devices of the same type on the local network and is therefore of type UInt32.
| YES | HighestActiveAlarmSeverity | UInt16 | PropertyType | Indication of the severity of the highest active alarm (0 = no active alarm – 1000 = possible error). Together with ActiveErrors, it provides a minimal error handling for devices without alarm support. However, the variable shall be filled even if alarms are supported. | --- | Mandatory | Read-Only | Table 8, element in Table 6 above. | n_EM_HighestActiveAlarmSeverity
| YES | ActiveErrors | ActiveErrorDataType[] | BaseDataVariableType | List of the active errors of the device. It provides a minimal error handling for devices without alarm support. However, the variable shall be filled even if alarms are supported. The ActiveErrorDataType is defined in EUROMAP 83. If there is no active error, the array is empty. | --- | Mandatory | Read-Only | Table 8, element in Table 6 above, further defined in Table 139. | st_EM_ActiveErrorDataType
| YES | ResetAllErrors | ---Method--- | ResetAllErrors() | Method to reset all errors of the device. | --- | Optional | --- | Table 8, element in Table 6 above. | b_EM_ResetAllErrors
| NO | ResetErrorById | ---Method--- | ResetErrorById([in] String Id);[in] String Id); | Method to reset one error of the device. | --- | Optional | --- | Table 8, element in Table 6 above. | Machine does not support single error reset.
| YES | OperatingMode | OperatingModeEnumeration | PropertyType | Actual operating mode of the TCD. | <enumeration> | Mandatory | Read-Only | Table 8, element in Table 6 aboe, see Table 11 enumeration further down. | n_EM_OperatingMode
| YES | HoursOfOperation | Double | AnalogItemType | Actual hours of operation | hours | Optional | Read-Only | Table 8, element in Table 6 above. | r_EM_HoursOfOperation
| YES | IdentifyDevice | ---Method--- | IdentifyDevice (); | The TCD on which this method is called shows itself by e.g. activation of a LED. | --- | Optional | --- | Table 8, element in Table 6 above. | b_EM_IdentifyDevice
| YES | SwitchOn | ---Method--- | SwitchOn (); | Main switch method of the TCD for switching on. OperatingMode shows the actual state of the device. | --- | Mandatory | --- | Table 8, element in Table 6 above. | b_EM_SwitchOn
| YES | SwitchOff | ---Method--- | SwitchOff (); | Main switch method of the TCD for switching off. OperatingMode shows the actual state of the device. | --- | Mandatory | --- | Table 8, element in Table 6 above. | b_EM_SwitchOff
| YES | ReduceToStandByOn | ---Method--- | ReduceToStandByOn (); | Activate the cooling down function on the TCD followed by switching off. OperatingMode shows the actual state of the device during the cooling down process. | --- | Optional | --- | Table 8, element in Table 6 above. | b_EM_ReduceToStandByOn
| NO | ReduceToStandByOff | ---Method--- | ReduceToStandByOff (); | Deactivate the cooling down function on the TCD. If it is already in progress, it will be interrupted and the device changes back to the last selected operating mode. | --- | Optional | --- | Table 8, element in Table 6 above. | TCU doesn't allow this. If cooldown is stopped, machine is stopped and must be restarted.
11: OperatingMode (Enumeration Values)
| YES | OTHER_0 | <enumeration> | 0 | Operating mode of the TCU is unknown | --- | --- | --- | Table 11, enumeration in Table 8 above.
| YES | READY_TO_OPERATE_1 | <enumeration> | 1 | TCU is ready to operate (heating, pump and cooling are switched off) | --- | --- | --- | Table 11, enumeration in Table 8 above.
| YES | NORMAL_OPERATION_2 | <enumeration> | 2 | TCU is running in normal operating mode | --- | --- | --- | Table 11, enumeration in Table 8 above.
| NO | LEAK_STOPPER_3 | <enumeration> | 3 | TCU is running in leak stopper operating mode | --- | --- | --- | Table 11, enumeration in Table 8 above.
| YES | MOULD_EVACUATION_4 | <enumeration> | 4 | TCU is carrying out a mould evacuation process | --- | --- | --- | Table 11, enumeration in Table 8 above.
| YES | PRESSURE_RELIEF_5 | <enumeration> | 5 | TCU is carrying out a pressure relief process | --- | --- | --- | Table 11, enumeration in Table 8 above.
| YES | COOLING_6 | <enumeration> | 6 | TCU is cooling down to StandbyTemperature and switch off | --- | --- | --- | Table 11, enumeration in Table 8 above.
| YES | SAFETY_COOLING_7 | <enumeration> | 7 | TCU is cooling down to SwitchingOffTemperature and switch off | --- | --- | --- | Table 11, enumeration in Table 8 above.
| NO | ECO_8 | <enumeration> | 8 | TCU is running in Eco operating mode (energy is saved via the reduced pump speed) | --- | --- | --- | Table 11, enumeration in Table 8 above.
| NO | BOOST_9 | <enumeration> | 9 | TCU is running in Boost operating mode (pump runs at maximum possible speed) | --- | --- | --- | Table 11, enumeration in Table 8 above.
12: DeviceZoneType (part of TCD_lnterfaceType)
| YES | Temperature | ---Object--- | ControlledParameterType | Setting and/or monitoring of the temperature in the main or return line (see InternalMeasuringPoint) or active external Sensor (ExternalSensorModeOn) | °C | Mandatory | --- | Table 12, element in Table 6 above.
| YES | InternalMeasuringPoint | UInt16 | MultiStateValueDiscreteType | This determines whether the temperature of the main or the return is to be controlled. | <enumeration> | Optional | Read/Write | Table 12, element in Table 6 above, see Table 13 enumeration further down. | n_EM_InternalMeasuringPoint
| YES | StandbyTemperature | Double | AnalogItemType | The standby value temperature is approached with the Method ReduceToStandByOn. | °C | Optional | Read/Write | Table 12, element in Table 6 above. | r_EM_StandbyTemperature
The TCD switches off.
| NO | SwitchingOffTemperature | Double | AnalogItemType | Defines the temperature to which the TCD must be cooled down before it switches off. | °C | Optional | Read/Write | Table 12, element in Table 6 above. | Not a restriction on this equipment.
| NO | TemperatureLimitation | Double | AnalogItemType | This setpoint is for temperature limitation of the mould circuit e.g. to protect the connected tubes or the downstream water distribution system. | °C | Optional | Read/Write | Table 12, element in Table 6 above. | Unknown purpose
| YES | TemperatureMainLine | Double | AnalogItemType | Actual temperature in the main line. | °C | Optional | Read-Only | Table 12, element in Table 6 above. | r_EM_TemperatureMainLine
| YES | TemperatureReturnLine | Double | AnalogItemType | Actual temperature in the return line. | °C | Optional | Read-Only | Table 12, element in Table 6 above. | r_EM_TemperatureReturnLine
| YES | TemperatureDifference | ---Object--- | MonitoredParameterType | Setting and/or monitoring of the temperature difference between return and main line. | °C | Optional | --- | Table 12, element in Table 6 above, MonitoredParameterType defined in Euromap 83, defined below Table 126A.
Positive if temperature in return line is higher than in main line.
| YES | FlowRate | ---Object--- | MonitoredParameterType | Setting and/or monitoring of the flow rate. | gal/min | Optional | --- | Table 12, element in Table 6 above, MonitoredParameterType defined in Euromap 83, defined below Table 126B.
| YES | PressureMainLine | Double | AnalogItemType | Actual pressure in the main line (Pressure return line + pump pressure). | psi | Optional | Read-Only | Table 12, element in Table 6 above. | r_EM_PressureMainLine
| YES | PressureReturnLine | Double | AnalogItemType | Actual pressure in the return line. | psi | Optional | Read-Only | Table 12, element in Table 6 above. | r_EM_PressureReturnLine
| YES | PressureDifference | ---Object--- | MonitoredParameterType | Setting and/or monitoring of the pressure difference between main and return line. | psi | Optional | --- | Table 12, element in Table 6 above, MonitoredParameterType defined in Euromap 83, defined below Table 126C.
| NO | ActualProcessPower | Double | AnalogItemType | Actual calculated process performance (from the view of the TCD: heating = positive value, cooling = negative value) | kW | Optional | Read-Only | Table 12, element in Table 6 above. | Cooling kW not available.
| YES | ActualRegulationRatio | Double | AnalogItemType | Actual Regulation Ratio (heating = positive value, cooling = negative value) | % | Optional | Read-Only | Table 12, element in Table 6 above. | r_EM_ActualRegulationRatio
| YES | DelayTimeAfterCooling | Double | AnalogItemType | Delay Time after cooling before switching off the TCD. | min | Optional | Read/Write | Table 12, element in Table 6 above. | r_EM_DelayTimeAfterCooling
| YES | PumpSpeed | ---Object--- | MonitoredParameterType | Setting and/or monitoring the speed of the pump in percent of maximum speed. | % | Optional | --- | Table 12, element in Table 6 above, MonitoredParameterType defined in Euromap 83, defined below Table 126D.
| YES | ActualPumpSpeedRPM | Double | AnalogItemType | Actual speed of the pump in revolutions per minute. | rpm | Optional | Read-Only | Table 12, element in Table 6 above. | r_EM_ActualPumpSpeedRPM
| YES | ActualPumpPower | Double | AnalogItemType | Actual power of the pump in kW. | kW | Optional | Read-Only | Table 12, element in Table 6 above. | r_EM_ActualPumpPower
| YES | PumpControlMode | UInt16 | MultiStateValueDiscreteType | Defines to which setpoint or function the pump is controlled. | <enumeration> | Optional | Read/Write | Table 12, element in Table 6 above, see Table 14 enumeration further down. | n_EM_PumpControlMode
| YES | ExternalSensor | ---Object--- | ExternalSensorType | ExternalSensor is an optional component from DeviceZoneType and includes variables for the operation with an external temperature sensor. The temperature sensor is connected at the TCD directly or the value can come from the connected machine. | --- | Optional | --- | Table 12, element in Table 6 above, see Table 15 type description further down.
| NO | LeakStopper | ---Object--- | LeakStopperType | LeakStopperType is an optional component of DeviceZoneType and is used for switching the leak stopper mode. | --- | Optional | --- | Table 12, element in Table 6 above, see Table 18 type description further down. | Leak stopper not available.
| YES | MouldEvacuation | ---Object--- | MouldEvacuationType | Includes parameters and nodes for mould evacuation. | --- | Optional | --- | Table 12, element in Table 6 above, see Table 19 type description further down.
| YES | MaintenanceInformation | ---Object--- | MaintenanceInformationType | Information on the maintenance status of heating, cooling, pump and fluid. | --- | Optional | --- | Table 12, element in Table 6 above, see Table 22 type description further down.
| NO | ExternalChannels | ---Object--- | ExternalChannelsType | This is a container for the external channel(s). | --- | Optional | --- | Table 12, element in Table 6 above, see Table 23 type description further down.
13: InternalMeasuringPoint (Enumeration Values)
| YES | MAIN_LINE | <enumeration> | 0 | Control of the forward flow temperature | --- | --- | --- | Table 13, enumeration in Table 12 above.
| YES | RETURN_LINE | <enumeration> | 1 | Control of the return flow temperature | --- | --- | --- | Table 13, enumeration in Table 12 above.
14: PumpControlMode (Enumeration Values)
| YES | NORMAL | <enumeration> | 0 | Normal Operation: fixed pump rotational speed. | --- | --- | --- | Table 14, enumeration in Table 12 above.
| YES | AUTO | <enumeration> | 1 | Automatic adjustment of the pump rotational speed. | --- | --- | --- | Table 14, enumeration in Table 12 above.
| YES | SPEED | <enumeration> | 2 | Speed controlled: the pump is controlled according to the specified nominal value PumpSpeed. | --- | --- | --- | Table 14, enumeration in Table 12 above.
| YES | FLOW | <enumeration> | 3 | Flow rate controlled: the pump is controlled according to the | --- | --- | --- | Table 14, enumeration in Table 12 above.
specified nominal value FlowRate
| YES | TEMP_DIFF | <enumeration> | 4 | Temperature difference controlled: the pump is controlled according to the specified nominal value TemperatureDifference. | --- | --- | --- | Table 14, enumeration in Table 12 above.
| YES | PRESS_DIFF | <enumeration> | 5 | Pressure difference controlled: the pump is controlled according to the specified nominal value PressureDifference. | --- | --- | --- | Table 14, enumeration in Table 12 above.
| YES | BOOST | <enumeration> | 6 | Boost mode: the pump is operated at the maximum possible rotational pump speed. | --- | --- | --- | Table 14, enumeration in Table 12 above.
15: ExternalSensorType (part of DeviceZoneType)
| YES | ActualValue | Double | AnalogItemType | Actual value of external temperature sensor. | °C | Mandatory | Read/Write | Table 15, element in Table 12 above. | r_EM_ExtSensorTypeActualValue
| YES | Used | Boolean | PropertyType | Return whether an external temperature sensor is used for control. | TRUE/FALSE | Mandatory | Read-Only | Table 15, element in Table 12 above. | b_EM_ExternalSensorTypeUsed
| YES | ExternalSensorModeOn | ---Method--- | ExternalSensorModeOn (); | Activate the mode where the external temperature sensor is used for temperature control. | --- | Mandatory | --- | Table 15, element in Table 12 above. | b_EM_ExternalSensorModeOn
| YES | ExternalSensorModeOff | ---Method--- | ExternalSensorModeOff (); | Deactivate the mode where the external temperature sensor is used for temperature control. | --- | Mandatory | --- | Table 15, element in Table 12 above. | b_EM_ExternalSensorModeOff
| YES | ThermocoupleType | UInt16 | MultiStateValueDiscreteType | This two Variables are used to specify the type of connected external temperature sensor and the used communication protocol between the sensor and the control system of the TCD. | <enumeration> | Mandatory | Read/Write | Table 15, element in Table 12 above, see Table 16 enumeration farther down. | n_EM_ThermocoupleType
| YES | CommunicationProtocolType | UInt16 | MultiStateValueDiscreteType | This two Variables are used to specify the type of connected external temperature sensor and the used communication protocol between the sensor and the control system of the TCD. | <enumeration> | Mandatory | Read/Write | Table 15, element in Table 12 above, see Table 17 enumeration farther down. | n_EM_CommunicationProtocolType
| NO | AutomaticModeSwitch | Boolean | PropertyType | Setting whether switching to external sensor is performed automatically (TRUE) or manually (FALSE). TRUE is when the external sensor is plugged regulated to this and again switched automatically when unplugging the internal measurement site. | hours | Optional | Read/Write | Table 15, element in Table 12 above. | Not implemented
| YES | ClosedLoopControl | ---Object--- | ClosedLoopControlType | With this Object of ClosedLoopControlType (defined in EUROMAP 83) the client can do settings for the closed loop control for the sensor. | --- | Optional | --- | Table 15, element in Table 12 above, defined in Euromap 83 and table 132 below.
16: ThermocoupleType (Enumeration Values)
| YES | OTHER | <enumeration> | 0 | Other sensor type | --- | --- | --- | Table 16, enumeration in Table 15 above.
| YES | E | <enumeration> | 1 | Type E sensor: NiCr-CuNi | --- | --- | --- | Table 16, enumeration in Table 15 above.
| YES | J | <enumeration> | 2 | Type J, L sensor: Fe-CuNi | --- | --- | --- | Table 16, enumeration in Table 15 above.
| YES | K | <enumeration> | 3 | Type K sensor: NiCr-Ni | --- | --- | --- | Table 16, enumeration in Table 15 above.
| YES | N | <enumeration> | 4 | Type N sensor: NiCrSi-NiSi | --- | --- | --- | Table 16, element in Table 15 above.
| YES | T | <enumeration> | 5 | Type T sensor: Cu-CuNi | --- | --- | --- | Table 16, element in Table 15 above.
| YES | PT100 | <enumeration> | 6 | Pt 100-Sensor | --- | --- | --- | Table 16, enumeration in Table 15 above.
17: CommunicationProtocolType (Enumeration Values)
| YES | OTHER | <enumeration> | 0 | Other connection type | --- | --- | --- | Table 17, enumeration in Table 15 above.
| YES | LOCAL | <enumeration> | 1 | Communication integrated in the local control system (local input) | --- | --- | --- | Table 17, enumeration in Table 15 above.
| YES | PROFIBUS | <enumeration> | 2 | Values via Profibus | --- | --- | --- | Table 17, enumeration in Table 15 above.
| YES | OPC_UA | <enumeration> | 3 | Values via OPC UA | --- | --- | --- | Table 17, enumeration in Table 15 above.
| YES | I2C | <enumeration> | 4 | Values via I2C | --- | --- | --- | Table 17, enumeration in Table 15 above.
| YES | CAN | <enumeration> | 5 | Values via CAN | --- | --- | --- | Table 17, enumeration in Table 15 above.
18: LeakStopperType (part of DeviceZoneType)
| NO | On | ---Method--- | On (); | Activate the leak stopper mode (emergency operation in case of leaks in the system) | --- | Mandatory | --- | Table 18, element in Table 12 above. | Not implemented
| NO | Off | ---Method--- | Off (); | Deactivate the leak stopper mode. | --- | Mandatory | --- | Table 18, element in Table 12 above. | Not implemented
19: MouldEvacuationType (part of DeviceZoneType)
| YES | On | ---Method--- | On (); | Activate evacuation mode. | --- | Mandatory | --- | Table 19, element in Table 12 above. | b_EM_MouldEvacuationOn
| YES | Off | ---Method--- | Off (); | Deactivate evacuation mode. | --- | Mandatory | --- | Table 19, element in Table 12 above. | b_EM_MouldEvacuationOff
| NO | TemperatureLimit | Double | AnalogItemType | Temperature Limitation of the mould evacuation. TCD is cooled to this temperature first if necessary. | °C | Optional | Read/Write | Table 19, element in Table 12 above. | Not implemented
| YES | Time | Double | AnalogItemType | Duration of the mould evacuation. | sec | Optional | Read/Write | Table 19, element in Table 12 above. | r_EM_MouldEvacuationTime
| YES | Sink | UInt16 | MultiStateValueDiscreteType | Defines where the medium is to be emptied. | <enumeration> | Optional | Read/Write | Table 19, element in Table 12 above, see Table 20 enumeration farther down. | n_EM_MouldEvacuationSink
| YES | Mode | UInt16 | MultiStateValueDiscreteType | Defines how the medium is to be emptied. | <enumeration> | Optional | Read/Write | Table 19, element in Table 12 above, see Table 21 enumeration farther down | n_EM_MouldEvacuationMode
20: Sink (Enumeration Values)
| YES | DRAIN | <enumeration> | 0 | Medium is passed into the cooling or system water outlet. | --- | --- | --- | Table 20, enumeration in Table 19 above.
| YES | TANK | <enumeration> | 1 | Medium is conducted in a separate outlet. | --- | --- | --- | Table 20, enumeration in Table 19 above.
21: Mode (Enumeration Values)
| YES | PUMP | <enumeration> | 0 | Evacuation by the pump. | --- | --- | --- | Table 21, enumeration in Table 19 above.
| YES | COMPRESSED_AIR | <enumeration> | 1 | Evacuation with compressed air. | --- | --- | --- | Table 21, enumeration in Table 19 above.
22: MaintenanceInformationType (part of DeviceZoneType)
| YES | Heating | ---Object--- | MaintenanceType | Defined in Euromap 83. | --- | Optional | --- | Table 22, element in Table 12 above, defined in Euromap 83, and below in Table 83:136A.
| YES | Cooling | ---Object--- | MaintenanceType | Defined in Euromap 83. | --- | Optional | --- | Table 22, element in Table 12 above, defined in Euromap 83, and below in Table 83:136B.
| YES | Pump | ---Object--- | MaintenanceType | Defined in Euromap 83. | --- | Optional | --- | Table 22, element in Table 12 above, defined in Euromap 83Table 22, element in Table 12 above, defined in Euromap 83, and below in Table 83:136C.
| NO | Fluid | ---Object--- | MaintenanceType | Defined in Euromap 83. | --- | Optional | --- | Table 22, element in Table 12 above, defined in Euromap 83. | Feature not available in machine.
23: ExternalChannelsType (part of DeviceZoneType)
| NO | 0:NodeVersion | String | PropertyType |  | --- | Mandatory | Read-Only | Table 23, element in Table 12 above. | Parent object was optional in Table 12. Not implemented.
| NO | ExternalChannel_<Nr> | ---Object--- | ExternalChannelType | Includes information for monitoring or controlling of external temperature, flow rate or pressure channels. (One zone of the TCD is split into several external channels). | --- | Optional | --- | Table 23, element in Table 12 above, see Table 24 type description further down. | Parent object was optional in Table 12. Not implemented.
| NO | GeneralModelChangeEventType | ---ObjectType--- |  |  | --- | --- | --- | Table 23, element in Table 12 above. | Parent object was optional in Table 12. Not implemented.
24: ExternalChannelsType (part of ExternalChannelsType)
| NO | SwitchOn | ---Method--- | SwitchOn (); | Switch method of the external channel for switching on. SwitchedOn shows the actual state of the channel. | --- | Optional | --- | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | SwitchOff | ---Method--- | SwitchOff (); | Switch method of the external channel for switching off. SwitchedOn shows the actual state of the channel. | --- | Optional | --- | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | SwitchedOn | Boolean | PropertyType | Information if the external channel is switched on. If the methods SwitchOn and SwitchOff are provided, also this Property shall be available. | --- | Optional | Read-Only | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | Temperature | ---Object--- | MonitoredParameterType | Setting and/or monitoring of the temperature. | °C | Optional | --- | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | TemperatureMainLine | Double | AnalogItemType | Actual temperature in the main line. | °C | Optional | Read-Only | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | TemperatureReturnLine | Double | AnalogItemType | Actual temperature in the return line. | °C | Optional | Read-Only | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | TemperatureDifference | ---Object--- | MonitoredParameterType | Setting and/or monitoring of the temperature difference between return and main line. Positive if temperature in return line is higher than in main line. | Δ°C | Optional | --- | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | FlowRate | ---Object--- | MonitoredParameterType | Setting and/or monitoring of the flow rate. | gal/min | Optional | --- | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | PressureMainLine | Double | AnalogItemType | Actual value of the pressure in the main line. | psi | Optional | Read-Only | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | PressureReturnLine | Double | AnalogItemType | Actual value of the pressure in the return line. | psi | Optional | Read-Only | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | PressureDifference | ---Object--- | MonitoredParameterType | Setting and/or monitoring of the pressure difference between main and return line. | Δpsi | Optional | --- | Table 24, element in Table 23 above. | Parent object was optional in Table 12. Not implemented.
| NO | ControlMode | UInt16 | MultiStateValueDiscreteType | Defines to which setpoint the external channel is controlled, | --- | Optional | Read-Write | Table 24, element in Table 23 above, see Table 25 enumeration farther down. | Parent object was optional in Table 12. Not implemented.
25: ControlMode (Enumeration Values)
| NO | NONE | <enumeration> | 0 | No control, only monitoring. | --- | --- | --- | Table 25, enumeration in Table 24 above. | Parent object was optional in Table 12. Not implemented.
| NO | TEMPERATURE | <enumeration> | 1 | Temperature controlled. | --- | --- | --- | Table 25, enumeration in Table 24 above. | Parent object was optional in Table 12. Not implemented.
| NO | FLOW | <enumeration> | 2 | Flow rate controlled. | --- | --- | --- | Table 25, enumeration in Table 24 above. | Parent object was optional in Table 12. Not implemented.
| NO | TEMP_DIFF | <enumeration> | 3 | Temperature difference controlled. | --- | --- | --- | Table 25, enumeration in Table 24 above. | Parent object was optional in Table 12. Not implemented.
| NO | PRESS_DIFF | <enumeration> | 4 | Pressure difference controlled. | --- | --- | --- | Table 25, enumeration in Table 24 above. | Parent object was optional in Table 12. Not implemented.
26: TCDHelpOffNormalAlarmType (part of TCD_lnterfaceType)
| YES | DeviceMappingNumber | UInt32 | PropertyType | The value of DeviceMappingNumber corresponds to the value given in the instance of the OperationType for assigning the alarm to a device. | --- | Mandatory | Read-Only | Table 26, element in Table 6 above, see Table 27 severity classes farther down. | n_EM_DeviceMappingNumber
27: Severity Classes of TCDHelpOffNormalAlarmType
| YES | 667-1000 | UInt32 |  | Messages of high urgency (error, system alarm): Limit values have been exceeded. The transgression has a direct influence on the operational safety of the unit. Acknowledgement: compulsory. | --- | --- | --- | Table 27, futher definining propety in Table 26 above.
| YES | 334-666 | UInt32 |  | Messages of medium urgency (warning, process alarm): Limit values have been exceeded. The transgression has no influence on the operational safety of the unit. Acknowledgement: not compulsory. | --- | --- | --- | Table 27, futher definining propety in Table 26 above.
| YES | 1-333 | UInt32 |  | Messages of low urgency (Information). | --- | --- | --- | Table 27, futher definining propety in Table 26 above.
83:125: IdentificationType (part of TCD_lnterfaceType)
| YES | 2:DeviceClass | String | PropertyType | The DeviceClass Property indicates in which domain or for what purpose a certain device is used. The Property is optional in OPC UA DI. Here it is overridden and made mandatory. The value is specified in the specific Companion Specification (e.g. "Hot Runner Device " for OPC 40082-2) The DeviceClass Property in the Identification Object shall have the value "Temperature Control Device". | --- | Mandatory | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | s_EM_DeviceClass
| YES | 2:Manufacturer | LocalizedText | PropertyType | The Manufacturer Property provides the name of the manufacturer of the machine (e.g. "Negri Bossi"). The Property is optional in OPC UA DI. Here it is overridden and made mandatory. | --- | Mandatory | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | s_EM_Manufacturer
| YES | 2:Model | LocalizedText | PropertyType | The Model Property represents the name of the machine type (e.g. "KM 1000-2500", "Allrounder"). The Property is optional in OPC UA DI. Here it is overridden and made mandatory. | --- | Mandatory | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | s_EM_Model
| YES | 2:SerialNumber | String | PropertyType | The SerialNumber Property represents the serial number of the machine (unique ID given by the manufacturer, e.g. "1240114"). The Property is optional in OPC UA DI. Here it is overridden and made mandatory. | --- | Mandatory | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | s_EM_SerialNumber
| NO | YearOfConstruction | UInt16 | PropertyType | The YearOfConstruction Property represents the year of construction of the machine (e.g. "2018"). | --- | Optional | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | Not known in machine.
3.47708333333333: MachineConfigurationType (part of TCD_lnterfaceType)
| YES | UserMachineName | 0:String | PropertyType | The UserMachineName Property represents the description of the machine given by the machine operator or OPC client (e.g. "machine 42"). | --- | Mandatory | Read-Write | Table 27 (Euromap 83), element in Table 6 above. | s_EM_UserMachineName (Retained)
| YES | LocationName | 0:String | PropertyType | The LocationName Property represents the description of the location of the machine given by the machine operator or OPC client (e.g. "plant 2, hall C"). | --- | Mandatory | Read-Write | Table 125 (Euromap 83), element in Table 6 above. | s_EM_LocationName (Retained)
| YES | TimeZoneOffset | 0:TimeZoneDataType | PropertyType | The TimeZoneOffset Property represents the difference of the local time to Coordinated Universal Time (UTC) given by the machine operator or OPC client. | --- | Mandatory | Read-Write | Table 125 (Euromap 83), element in Table 6 above. | st_EM_TimeZoneOffset
| YES | SetMachineTime | ---Method--- | SetMachineTime ( | The SetMachineTime Method allows setting the server time together with TimeZoneOffset. | --- | Mandatory |  | Table 125 (Euromap 83), element in Table 6 above. | b_EM_SetMachineTime
[in] 0:DateTime DateTime
[in] 0:TimeZoneDataType TimeZoneOffset);
| NO | PageDirectory | PageEntryDataType[] | PropertyType | The PageDirectory Property is an array and represents a list of the pages that are implemented in the machine control system and are shown on the screen of the machine. | --- | Optional | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | Feature not feasible.
| NO | GetPage | ---Method--- | GetPage ( | Method for retrieving the image of a page of the control system. | --- | Optional | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | Feature not feasible.
[in] 0:String Id
[out] 0:Image Page);
| NO | GetCurrentPage | ---Method--- | GetCurrentPage ( | Method for retrieving a screenshot of the control system with the currently shown contents. | --- | Optional | Read-Only | Table 125 (Euromap 83), element in Table 6 above. | Feature not feasible.
[in] 0:UInt32 VisualisationUnit
[out] 0:Image Page);
83:126A: MonitoredParameterType, (part of DeviceZoneType, Temperature)
| YES | ActualValue | Double | AnalogItemType | Actual value of the monitored parameter (unit given in AnalogItemType). | --- | Mandatory | Read-Only | Table 126A (Euromap 83), element in Table 12 above. | r_EM_TemperatureActualValue
| YES | SetValue | Double | AnalogItemType | Set/nominal/target value of the monitored parameter. The value of this variable is writeable by the client. As the MonitoredParameterType is not used to control parameters, this is only for information/Process monitoring and not for changing setting on the device. | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | r_EM_TemperatureSetValue
| NO | SetRampUp | Double | AnalogItemType | Indication if a SetValue that is higher than the actual value shall be reached as fast as possible (SetRampUp =0) or within a given value change per time (e.g. SetRampUp = 2 K/s). | --- | Optional | Read-Only | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampDown | Double | AnalogItemType | Indication if SetValue that is lower than the actual value shall be reached as fast as possible (SetRampDown =0) or within a given value change per time (e.g. SetRampDown = 2 K/s). NOTE: Always positive value. | --- | Optional | Read-Only | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| YES | MinValue | Double | AnalogItemType | These parameters are used to define limits for the monitored parameter. Exceeding the (relative) tolerance values creates a warning while exceeding the (absolute) Min/MaxValues leads to an alarm from type MonitoredParameterAlarmType and/or perhaps other actions on the machine (e.g. switching off the heating, stopping of movements) as defined by the severity level. With UpperTolerance2 and LowerTolerance2 a second tolerance band can be defined. NOTE: When UpperTolerance and/or LowerTolerance are used, the SetValue shall be also given. NOTE: When UpperTolerance2 and/or LowerTolerance2 are used, UpperTolerance and/or LowerTolerance shall be also given. UpperTolerance2 shall be between UpperTolerance and MaxValue. LowerTolerance2 shall be between LowerTolerance and MinValue. | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | r_EM_TemperatureMinValue
| YES | MaxValue | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | r_EM_TemperatureMaxValue
| NO | UpperTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| YES | Status | UInt16 | MultiStateValueDiscreteType | Information if the ActualValue is within the tolerances or has passed a tolerance or min/max value. The TypeDefinition is MultiStateValueDiscreteType, so the Properties EnumValues and ValueAsText shall be filled with the supported values out of Table 127. | --- | Optional | Read-Only | Table 126A (Euromap 83), element in Table 12 above, see Table 83:127 enumeration further down. | n_EM_TemperatureStatus
| NO | AutomaticMonitoring | Boolean | PropertyType | Determination if monitoring tolerance parameters are determined by auto-tuning itself (TRUE) or can be manually adjusted (FALSE). If TRUE the monitoring tolerance parameters are determined by auto-tuning regarding the set monitoring sensitivity (if used). In this case, the tolerance parameters shall then be not writeable. | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MonitoringSensitivity | UInt16 | MultiStateValueDiscreteType | The monitoring sensitivity defines how closely the tolerances are set during the automatic limit setting. | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | AlarmSuppression | UInt16 | MultiStateValueDiscreteType | The alarm suppression deactivates alarms of a monitored parameter e.g. during start up or a setpoint jump. | --- | Optional | Read-Write | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Reset Monitoring | ---Method--- |  | With this method the tolerance values are set according to the actual value and the set monitoring sensitivity. This can be used e.g. after a process change with new SetValue to adapt the monitoring. | --- | Optional |  | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | ControlledParameterType | ObjectType |  | The ControlledParameterType is used for process parameters that are controlled by the client by writing a set value and optional ramps and parameters for closed loop control. | --- |  |  | Table 126A (Euromap 83), element in Table 12 above. | Feature not available in machine.
83:126B: MonitoredParameterType, (part of DeviceZoneType, TemperatureDifference)
| YES | ActualValue | Double | AnalogItemType | Actual value of the monitored parameter (unit given in AnalogItemType). | --- | Mandatory | Read-Only | Table 126B (Euromap 83), element in Table 12 above. | r_EM_TemperatureDiffActualValue
| NO | SetValue | Double | AnalogItemType | Set/nominal/target value of the monitored parameter. The value of this variable is writeable by the client. As the MonitoredParameterType is not used to control parameters, this is only for information/Process monitoring and not for changing setting on the device. | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampUp | Double | AnalogItemType | Indication if a SetValue that is higher than the actual value shall be reached as fast as possible (SetRampUp =0) or within a given value change per time (e.g. SetRampUp = 2 K/s). | --- | Optional | Read-Only | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampDown | Double | AnalogItemType | Indication if SetValue that is lower than the actual value shall be reached as fast as possible (SetRampDown =0) or within a given value change per time (e.g. SetRampDown = 2 K/s). NOTE: Always positive value. | --- | Optional | Read-Only | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MinValue | Double | AnalogItemType | These parameters are used to define limits for the monitored parameter. Exceeding the (relative) tolerance values creates a warning while exceeding the (absolute) Min/MaxValues leads to an alarm from type MonitoredParameterAlarmType and/or perhaps other actions on the machine (e.g. switching off the heating, stopping of movements) as defined by the severity level. With UpperTolerance2 and LowerTolerance2 a second tolerance band can be defined. NOTE: When UpperTolerance and/or LowerTolerance are used, the SetValue shall be also given. NOTE: When UpperTolerance2 and/or LowerTolerance2 are used, UpperTolerance and/or LowerTolerance shall be also given. UpperTolerance2 shall be between UpperTolerance and MaxValue. LowerTolerance2 shall be between LowerTolerance and MinValue. | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MaxValue | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Status | UInt16 | MultiStateValueDiscreteType | Information if the ActualValue is within the tolerances or has passed a tolerance or min/max value. The TypeDefinition is MultiStateValueDiscreteType, so the Properties EnumValues and ValueAsText shall be filled with the supported values out of Table 127. | --- | Optional | Read-Only | Table 126B (Euromap 83), element in Table 12 above, see Table 83:127 enumeration further down. | Feature not available in machine.
| NO | AutomaticMonitoring | Boolean | PropertyType | Determination if monitoring tolerance parameters are determined by auto-tuning itself (TRUE) or can be manually adjusted (FALSE). If TRUE the monitoring tolerance parameters are determined by auto-tuning regarding the set monitoring sensitivity (if used). In this case, the tolerance parameters shall then be not writeable. | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MonitoringSensitivity | UInt16 | MultiStateValueDiscreteType | The monitoring sensitivity defines how closely the tolerances are set during the automatic limit setting. | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | AlarmSuppression | UInt16 | MultiStateValueDiscreteType | The alarm suppression deactivates alarms of a monitored parameter e.g. during start up or a setpoint jump. | --- | Optional | Read-Write | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Reset Monitoring | ---Method--- |  | With this method the tolerance values are set according to the actual value and the set monitoring sensitivity. This can be used e.g. after a process change with new SetValue to adapt the monitoring. | --- | Optional |  | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | ControlledParameterType | ObjectType |  | The ControlledParameterType is used for process parameters that are controlled by the client by writing a set value and optional ramps and parameters for closed loop control. | --- |  |  | Table 126B (Euromap 83), element in Table 12 above. | Feature not available in machine.
83:126C: MonitoredParameterType, (part of DeviceZoneType, FlowRate)
| YES | ActualValue | Double | AnalogItemType | Actual value of the monitored parameter (unit given in AnalogItemType). | --- | Mandatory | Read-Only | Table 126C (Euromap 83), element in Table 12 above. | r_EM_FlowRateActualValue
| NO | SetValue | Double | AnalogItemType | Set/nominal/target value of the monitored parameter. The value of this variable is writeable by the client. As the MonitoredParameterType is not used to control parameters, this is only for information/Process monitoring and not for changing setting on the device. | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampUp | Double | AnalogItemType | Indication if a SetValue that is higher than the actual value shall be reached as fast as possible (SetRampUp =0) or within a given value change per time (e.g. SetRampUp = 2 K/s). | --- | Optional | Read-Only | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampDown | Double | AnalogItemType | Indication if SetValue that is lower than the actual value shall be reached as fast as possible (SetRampDown =0) or within a given value change per time (e.g. SetRampDown = 2 K/s). NOTE: Always positive value. | --- | Optional | Read-Only | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MinValue | Double | AnalogItemType | These parameters are used to define limits for the monitored parameter. Exceeding the (relative) tolerance values creates a warning while exceeding the (absolute) Min/MaxValues leads to an alarm from type MonitoredParameterAlarmType and/or perhaps other actions on the machine (e.g. switching off the heating, stopping of movements) as defined by the severity level. With UpperTolerance2 and LowerTolerance2 a second tolerance band can be defined. NOTE: When UpperTolerance and/or LowerTolerance are used, the SetValue shall be also given. NOTE: When UpperTolerance2 and/or LowerTolerance2 are used, UpperTolerance and/or LowerTolerance shall be also given. UpperTolerance2 shall be between UpperTolerance and MaxValue. LowerTolerance2 shall be between LowerTolerance and MinValue. | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MaxValue | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Status | UInt16 | MultiStateValueDiscreteType | Information if the ActualValue is within the tolerances or has passed a tolerance or min/max value. The TypeDefinition is MultiStateValueDiscreteType, so the Properties EnumValues and ValueAsText shall be filled with the supported values out of Table 127. | --- | Optional | Read-Only | Table 126C (Euromap 83), element in Table 12 above, see Table 83:127 enumeration further down. | Feature not available in machine.
| NO | AutomaticMonitoring | Boolean | PropertyType | Determination if monitoring tolerance parameters are determined by auto-tuning itself (TRUE) or can be manually adjusted (FALSE). If TRUE the monitoring tolerance parameters are determined by auto-tuning regarding the set monitoring sensitivity (if used). In this case, the tolerance parameters shall then be not writeable. | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MonitoringSensitivity | UInt16 | MultiStateValueDiscreteType | The monitoring sensitivity defines how closely the tolerances are set during the automatic limit setting. | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | AlarmSuppression | UInt16 | MultiStateValueDiscreteType | The alarm suppression deactivates alarms of a monitored parameter e.g. during start up or a setpoint jump. | --- | Optional | Read-Write | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Reset Monitoring | ---Method--- |  | With this method the tolerance values are set according to the actual value and the set monitoring sensitivity. This can be used e.g. after a process change with new SetValue to adapt the monitoring. | --- | Optional |  | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | ControlledParameterType | ObjectType |  | The ControlledParameterType is used for process parameters that are controlled by the client by writing a set value and optional ramps and parameters for closed loop control. | --- |  |  | Table 126C (Euromap 83), element in Table 12 above. | Feature not available in machine.
83:126D: MonitoredParameterType, (part of DeviceZoneType, PressureDifference)
| YES | ActualValue | Double | AnalogItemType | Actual value of the monitored parameter (unit given in AnalogItemType). | --- | Mandatory | Read-Only | Table 126D (Euromap 83), element in Table 12 above. | r_EM_PressureDiffActualValue
| NO | SetValue | Double | AnalogItemType | Set/nominal/target value of the monitored parameter. The value of this variable is writeable by the client. As the MonitoredParameterType is not used to control parameters, this is only for information/Process monitoring and not for changing setting on the device. | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampUp | Double | AnalogItemType | Indication if a SetValue that is higher than the actual value shall be reached as fast as possible (SetRampUp =0) or within a given value change per time (e.g. SetRampUp = 2 K/s). | --- | Optional | Read-Only | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampDown | Double | AnalogItemType | Indication if SetValue that is lower than the actual value shall be reached as fast as possible (SetRampDown =0) or within a given value change per time (e.g. SetRampDown = 2 K/s). NOTE: Always positive value. | --- | Optional | Read-Only | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MinValue | Double | AnalogItemType | These parameters are used to define limits for the monitored parameter. Exceeding the (relative) tolerance values creates a warning while exceeding the (absolute) Min/MaxValues leads to an alarm from type MonitoredParameterAlarmType and/or perhaps other actions on the machine (e.g. switching off the heating, stopping of movements) as defined by the severity level. With UpperTolerance2 and LowerTolerance2 a second tolerance band can be defined. NOTE: When UpperTolerance and/or LowerTolerance are used, the SetValue shall be also given. NOTE: When UpperTolerance2 and/or LowerTolerance2 are used, UpperTolerance and/or LowerTolerance shall be also given. UpperTolerance2 shall be between UpperTolerance and MaxValue. LowerTolerance2 shall be between LowerTolerance and MinValue. | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MaxValue | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Status | UInt16 | MultiStateValueDiscreteType | Information if the ActualValue is within the tolerances or has passed a tolerance or min/max value. The TypeDefinition is MultiStateValueDiscreteType, so the Properties EnumValues and ValueAsText shall be filled with the supported values out of Table 127. | --- | Optional | Read-Only | Table 126D (Euromap 83), element in Table 12 above, see Table 83:127 enumeration further down. | Feature not available in machine.
| NO | AutomaticMonitoring | Boolean | PropertyType | Determination if monitoring tolerance parameters are determined by auto-tuning itself (TRUE) or can be manually adjusted (FALSE). If TRUE the monitoring tolerance parameters are determined by auto-tuning regarding the set monitoring sensitivity (if used). In this case, the tolerance parameters shall then be not writeable. | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MonitoringSensitivity | UInt16 | MultiStateValueDiscreteType | The monitoring sensitivity defines how closely the tolerances are set during the automatic limit setting. | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | AlarmSuppression | UInt16 | MultiStateValueDiscreteType | The alarm suppression deactivates alarms of a monitored parameter e.g. during start up or a setpoint jump. | --- | Optional | Read-Write | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Reset Monitoring | ---Method--- |  | With this method the tolerance values are set according to the actual value and the set monitoring sensitivity. This can be used e.g. after a process change with new SetValue to adapt the monitoring. | --- | Optional |  | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | ControlledParameterType | ObjectType |  | The ControlledParameterType is used for process parameters that are controlled by the client by writing a set value and optional ramps and parameters for closed loop control. | --- |  |  | Table 126D (Euromap 83), element in Table 12 above. | Feature not available in machine.
83:126E: MonitoredParameterType, (part of DeviceZoneType, PumpSpeed)
| YES | ActualValue | Double | AnalogItemType | Actual value of the monitored parameter (unit given in AnalogItemType). | --- | Mandatory | Read-Only | Table 126E (Euromap 83), element in Table 12 above. | r_EM_PumpSpeedActualValue
| NO | SetValue | Double | AnalogItemType | Set/nominal/target value of the monitored parameter. The value of this variable is writeable by the client. As the MonitoredParameterType is not used to control parameters, this is only for information/Process monitoring and not for changing setting on the device. | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampUp | Double | AnalogItemType | Indication if a SetValue that is higher than the actual value shall be reached as fast as possible (SetRampUp =0) or within a given value change per time (e.g. SetRampUp = 2 K/s). | --- | Optional | Read-Only | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | SetRampDown | Double | AnalogItemType | Indication if SetValue that is lower than the actual value shall be reached as fast as possible (SetRampDown =0) or within a given value change per time (e.g. SetRampDown = 2 K/s). NOTE: Always positive value. | --- | Optional | Read-Only | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MinValue | Double | AnalogItemType | These parameters are used to define limits for the monitored parameter. Exceeding the (relative) tolerance values creates a warning while exceeding the (absolute) Min/MaxValues leads to an alarm from type MonitoredParameterAlarmType and/or perhaps other actions on the machine (e.g. switching off the heating, stopping of movements) as defined by the severity level. With UpperTolerance2 and LowerTolerance2 a second tolerance band can be defined. NOTE: When UpperTolerance and/or LowerTolerance are used, the SetValue shall be also given. NOTE: When UpperTolerance2 and/or LowerTolerance2 are used, UpperTolerance and/or LowerTolerance shall be also given. UpperTolerance2 shall be between UpperTolerance and MaxValue. LowerTolerance2 shall be between LowerTolerance and MinValue. | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MaxValue | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | UpperTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | LowerTolerance2 | Double | AnalogItemType |  | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Status | UInt16 | MultiStateValueDiscreteType | Information if the ActualValue is within the tolerances or has passed a tolerance or min/max value. The TypeDefinition is MultiStateValueDiscreteType, so the Properties EnumValues and ValueAsText shall be filled with the supported values out of Table 127. | --- | Optional | Read-Only | Table 126E (Euromap 83), element in Table 12 above, see Table 83:127 enumeration further down. | Feature not available in machine.
| NO | AutomaticMonitoring | Boolean | PropertyType | Determination if monitoring tolerance parameters are determined by auto-tuning itself (TRUE) or can be manually adjusted (FALSE). If TRUE the monitoring tolerance parameters are determined by auto-tuning regarding the set monitoring sensitivity (if used). In this case, the tolerance parameters shall then be not writeable. | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | MonitoringSensitivity | UInt16 | MultiStateValueDiscreteType | The monitoring sensitivity defines how closely the tolerances are set during the automatic limit setting. | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | AlarmSuppression | UInt16 | MultiStateValueDiscreteType | The alarm suppression deactivates alarms of a monitored parameter e.g. during start up or a setpoint jump. | --- | Optional | Read-Write | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | Reset Monitoring | ---Method--- |  | With this method the tolerance values are set according to the actual value and the set monitoring sensitivity. This can be used e.g. after a process change with new SetValue to adapt the monitoring. | --- | Optional |  | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
| NO | ControlledParameterType | ObjectType |  | The ControlledParameterType is used for process parameters that are controlled by the client by writing a set value and optional ramps and parameters for closed loop control. | --- |  |  | Table 126E (Euromap 83), element in Table 12 above. | Feature not available in machine.
83:127: Status (Enumeration Values)
| YES | NONE | <enumeration> | 0 | No monitoring. | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | UNKNOWN | <enumeration> | 1 | Status not known, e.g. because of broken sensor. | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | BELOW_MIN_VALUE | <enumeration> | 2 | ActualValue is below MinValue. | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | BELOW_LOWER_TOLERANCE2 | <enumeration> | 3 | ActualValue is below LowerTolerance2. | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | BELOW_LOWER_TOLERANCE | <enumeration> | 4 | ActualValue is below LowerTolerance | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | WITHIN_TOLERANCE | <enumeration> | 5 | ActualValue is between LowerTolerance and UpperTolerance | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | ABOVE_UPPER_TOLERANCE | <enumeration> | 6 | ActualValue is above UpperTolerance | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | ABOVE_UPPER_TOLERANCE2 | <enumeration> | 7 | ActualValue is above UpperTolerance2 | --- | --- | --- | Table 127, enumeration in Tables 126 above.
| YES | ABOVE_MAX_VALUE | <enumeration> | 8 | ActualValue is above MinValue | --- | --- | --- | Table 127, enumeration in Tables 126 above.
83:132: ClosedLoopControlType (part of ExternalSensorType)
| YES | PIDParameters | PIDParametersDataType[] | PropertyType | PID Parameters as array if several input signals (sensors) are used for the control. | --- | Optional | Read-Write | Table 132 (Euromap 83), element in Table 15 above, see table 133 below.
| YES | AutomaticControllerMode | Boolean | PropertyType | Determination if PID Parameters are determined by auto-tuning itself (TRUE) or can be manually adjusted (FALSE). | --- | Optional | Read-Write | Table 132 (Euromap 83), element in Table 15 above. | b_EM_AutomaticControllerMode
| YES | AutoTuningActive | Boolean | PropertyType | This Property informs if the automatic tuning is currently active. TRUE during automatic tuning, FALSE when automatic tuning is finished (new PID parameters are set, if necessary). If an error occurs during automatic tuning, the PID parameters will not be changed, AutoTuningActive goes back to FALSE and an alarm may be sent. | --- | Optional | Read-Only | Table 132 (Euromap 83), element in Table 15 above. | b_EM_AutoTuningActive
| YES | AutoTuningOn | ---Method--- | AutoTuningOn (); | Starts the self-optimisation of the controller. | --- | Optional |  | Table 132 (Euromap 83), element in Table 15 above. | b_EM_AutoTuningOn
| YES | AutoTuningOff | ---Method--- | AutoTuningOff (); | Stops an already active self-optimisation process (no control parameters are changed) | --- | Optional |  | Table 132 (Euromap 83), element in Table 15 above. | b_EM_AutoTuningOff
83:133: PIDParametersDataType[] (part of ClosedLoopControlType)
| YES | P | Double |  | P parameter | --- | Optional | Read-Write | Table 133 (Euromap 83), element in Table 132 above. | r_EM_PID_P
| YES | I | Double |  | I parameter | --- | Optional | Read-Write | Table 133 (Euromap 83), element in Table 132 above. | r_EM_PID_I
| YES | D | Double |  | D parameter | --- | Optional | Read-Write | Table 133 (Euromap 83), element in Table 132 above. | r_EM_PID_D
83:132A: MaintenanceType (part of MaintenanceInformationType, Heating)
| YES | Status | MaintenanceStatusEnumeration | PropertyType | Maintenance status of the machine/device/component (represented by the parent element). | --- | Mandatory | Read-Only | Table 136A (Euromap 83), element in Table 22 above, enumeration in Table 137 below. | n_EM_Heating_Status
| YES | AdditionalInformation | String | PropertyType | Additional information on the necessary maintenance. Can be also a link to another document. | --- | Optional | Read-Only | Table 136A (Euromap 83), element in Table 22 above. | s_EM_Heating_AdditionalInfo
| YES | Interval | Double | AnalogItem | Regular interval between two maintenances. Use of AnalogItemType for flexible units (e.g. months, days, operating hours, m). | --- | Optional | Read-Only | Table 136A (Euromap 83), element in Table 22 above. | r_EM_Heating_Interval
| YES | RemainingInterval | Double | AnalogItem | Interval before next maintenance is due. | --- | Optional | Read-Only | Table 136A (Euromap 83), element in Table 22 above. | r_EM_Heating_RemainingInterval
| YES | Reset | ---Method--- | Reset (); | This Method sets the RemainingInterval to Interval and Status to NOT_DUE_0. | --- | Mandatory |  | Table 136A (Euromap 83), element in Table 22 above. | b_EM_Heating_Reset
| YES | TotalOperation | Double | AnalogItem | Same unit as Interval. How long is the component running in total. | --- | Optional | Read-Only | Table 136A (Euromap 83), element in Table 22 above. | r_EM_Heating_TotalOperation
83:132B: MaintenanceType (part of MaintenanceInformationType, Cooling)
| YES | Status | MaintenanceStatusEnumeration | PropertyType | Maintenance status of the machine/device/component (represented by the parent element). | --- | Mandatory | Read-Only | Table 136B (Euromap 83), element in Table 22 above, enumeration in Table 137 below. | n_EM_Cooling_Status
| YES | AdditionalInformation | String | PropertyType | Additional information on the necessary maintenance. Can be also a link to another document. | --- | Optional | Read-Only | Table 136B (Euromap 83), element in Table 22 above. | s_EM_Cooling_AdditionalInfo
| YES | Interval | Double | AnalogItem | Regular interval between two maintenances. Use of AnalogItemType for flexible units (e.g. months, days, operating hours, m). | --- | Optional | Read-Only | Table 136B (Euromap 83), element in Table 22 above. | r_EM_Cooling_Interval
| YES | RemainingInterval | Double | AnalogItem | Interval before next maintenance is due. | --- | Optional | Read-Only | Table 136B (Euromap 83), element in Table 22 above. | r_EM_Cooling_RemainingInterval
| YES | Reset | ---Method--- | Reset (); | This Method sets the RemainingInterval to Interval and Status to NOT_DUE_0. | --- | Mandatory |  | Table 136B (Euromap 83), element in Table 22 above. | b_EM_Cooling_Reset
| YES | TotalOperation | Double | AnalogItem | Same unit as Interval. How long is the component running in total. | --- | Optional | Read-Only | Table 136B (Euromap 83), element in Table 22 above. | r_EM_Cooling_TotalOperation
83:132C: MaintenanceType (part of MaintenanceInformationType, Pump)
| YES | Status | MaintenanceStatusEnumeration | PropertyType | Maintenance status of the machine/device/component (represented by the parent element). | --- | Mandatory | Read-Only | Table 136C (Euromap 83), element in Table 22 above, enumeration in Table 137 below. | n_EM_Pump_Status
| YES | AdditionalInformation | String | PropertyType | Additional information on the necessary maintenance. Can be also a link to another document. | --- | Optional | Read-Only | Table 136C (Euromap 83), element in Table 22 above. | s_EM_Pump_AdditionalInfo
| YES | Interval | Double | AnalogItem | Regular interval between two maintenances. Use of AnalogItemType for flexible units (e.g. months, days, operating hours, m). | --- | Optional | Read-Only | Table 136C (Euromap 83), element in Table 22 above. | r_EM_Pump_Interval
| YES | RemainingInterval | Double | AnalogItem | Interval before next maintenance is due. | --- | Optional | Read-Only | Table 136C (Euromap 83), element in Table 22 above. | r_EM_Pump_RemainingInterval
| YES | Reset | ---Method--- | Reset (); | This Method sets the RemainingInterval to Interval and Status to NOT_DUE_0. | --- | Mandatory |  | Table 136C (Euromap 83), element in Table 22 above. | b_EM_Pump_Reset
| YES | TotalOperation | Double | AnalogItem | Same unit as Interval. How long is the component running in total. | --- | Optional | Read-Only | Table 136C (Euromap 83), element in Table 22 above. | r_EM_Pump_TotalOperation
83:137: Status (Enumeration Values of MaintenanceStatusEnumeration)
| YES | NOT_DUE | <enumeration> | 0 | Maintenance of the device/component is not due. | --- | --- | --- | Table 137, enumeration in Tables 132s above.
| YES | WARNING | <enumeration> | 1 | Maintenance of the device/component is due in the near future. | --- | --- | --- | Table 137, enumeration in Tables 132s above.
| YES | DUE | <enumeration> | 2 | Maintenance of the device/component is due. | --- | --- | --- | Table 137, enumeration in Tables 132s above.
83:139: ActiveErrorDataType (part of OperationType)
| YES | Id | String |  | Unique identifier defined by manufacturer. | --- | Mandatory | Read-Only | Table 139 (Euromap 83), element in Table 8 above.
| YES | Severity | UInt16 |  | Severity as defined in the BaseEventType (1 = low – 1000 = high). | --- | Mandatory | Read-Only | Table 139 (Euromap 83), element in Table 8 above.
| YES | Message | LocalizedText |  | Message giving information about the error. | --- | Mandatory | Read-Only | Table 139 (Euromap 83), element in Table 8 above.

## EM Alarms
EUROMAP ALARMS
TCDHelpOffNormalAlarmType (part of TCD_lnterfaceType)
DeviceMappingNumber
ID | LINKED ALARM TAG | DESCRIPTION
1 | b_ALM_IO_HMI_ConnectionFailure | HMI Connection Failure
2 | b_ALM_IO_ModuleLinkFailure | IO Module Link Failure
3 | b_ALM_IO_HardwareMismatch | IO Module Hardware Mismatch
4 | b_ALM_IO_ModuleInternalFailure | IO Module Internal Failure
5 | b_ALM_IO_PointFailure | IO Point Failure
6 | b_ALM_PowerSupplyLow | Power Supply Voltage Low
7 | b_ALM_LogicSupplyLow | Logic Supply Voltage Low
8 | b_ALM_Overtemperature | Overtemperature
9 | b_ALM_HeaterContactorStuckClosed | Heater Contactor Stuck Closed
10 | b_ALM_FactoryTempHigh | High Temperature - Factory Limit
11 | b_ALM_Unbranded | Unbranded
12 | b_ALM_OptionsNotSet | Options Not Set
13 | b_ALM_PhaseMonitor | Phase Monitor
14 | b_ALM_PumpContactorStuckClosed | Pump Contactor Stuck Closed
15 | b_ALM_HeaterContactorStuckOpen | Heater Contactor Stuck Open
16 | b_ALM_PumpContactorStuckOpen | Pump Contactor Stuck Open
17 | b_ALM_PressureTooHigh | Pressure Too High
18 | b_ALM_ElecPanelTooHot | Electrical Panel Too Hot
19 | b_ALM_FactoryTempLow | Low Temperature - Factory Limit
20 | b_ALM_Brownout | Brownout Occurred
21 | b_ALM_UserTempHigh | High Temperature - User Limit
22 | b_ALM_UserTempLow | Low Temperature - User Limit
23 | b_ALM_LowPressureStandbyTimeout | Low Pressure Standby Timeout
24 | b_ALM_LowPressureStrikeout | Low Pressure Strikeout
25 | b_ALM_PumpOverload | Pump Overload
26 | b_ALM_FlowmeterLowFlow | Flowmeter Bad Flow
27 | b_ALM_SupplyRTD_Open | Supply RTD - Open Circuit
28 | b_ALM_SupplyRTD_Shorted | Supply RTD -Short Circuit
29 | b_ALM_SupplyRTD_Other | Supply RTD - Channel Error
30 | b_ALM_ReturnRTD_Open | Return RTD - Open Circuit
31 | b_ALM_ReturnRTD_Shorted | Return RTD - Short Circuit
32 | b_ALM_ReturnRTD_Other | Return RTD - Channel Error
33 | b_ALM_RemoteRTD_Open | Remote RTD - Open Circuit
34 | b_ALM_RemoteRTD_Shorted | Remote RTD - Short Circuit
35 | b_ALM_RemoteRTD_Other | Remote RTD - Channel Error
36 | b_ALM_AnaProcInHigh | Analog Process Input - High Signal
37 | b_ALM_AnaProcInLow | Analog Process Input - Low Signal
38 | b_ALM_AnaProcInOther | Analog Process Input - Channel Error
39 | b_ALM_NetProcHigh | Network Process Temperature - High Signal
40 | b_ALM_NetProcLow | Network Process Temperature - Low Signal
41 | b_ALM_NetProcHeartbeat | Network Process Heartbeat Lost
42 | b_ALM_AnaSP_High | Analog Setpoint - High Signal
43 | b_ALM_AnaSP_Low | Analog Setpoint - Low Signal
44 | b_ALM_AnaSP_Other | Analog Setpoint - Channel Error
45 | b_ALM_NetSP_High | Network Setpoint - High Signal
46 | b_ALM_NetSP_Low | Network Setpoint - Low Signal
47 | b_ALM_NetSP_Heartbeat | Network Setpoint - Heartbeat Lost
48 | b_ALM_PressureBelowMinimum | System Pressure Below Minimum
49 | b_ALM_PressureNotHighEnough | System Pressure Not High Enough
50 | b_ALM_ReturnTransducerHigh | Return Transducer - High Signal
51 | b_ALM_ReturnTransducerLow | Return Transducer - Low Signal
52 | b_ALM_ReturnTransducerOther | Return Transducer - Channel Error
53 | b_ALM_SupplyTransducerHigh | Supply Transducer - High Signal
54 | b_ALM_SupplyTransducerLow | Supply Transducer - Low Signal
55 | b_ALM_SupplyTransducerOther | Supply Transducer - Channel Error
56 | b_ALM_AnaFlowmeterHigh | Analog Flowmeter - High Signal
57 | b_ALM_AnaFlowmeterLow | Analog Flowmeter - Low Signal
58 | b_ALM_AnaFlowmeterOther | Analog Flowmeter - Channel Error
59 | b_ALM_HighDeviation | Process Temperature High Deviation
60 | b_ALM_LowDeviation | Process Temperature Low Deviation
61 | b_ALM_NetworkHeartbeatLost | Network Heartbeat Lost
62 | b_ALM_RemoteSlaveAlarmActive | Bank Slave Alarm Active
63 | b_ALM_RampSoakPaused | Ramp Soak Paused
64 | b_ALM_PID_AT_InitOutputTooHigh | PID Autotune Failed, Starting Control Output Too High
65 | b_ALM_PID_AT_ProcResponseSlow | PID Autotune Failed, Process Response Too Slow
66 | b_ALM_PID_AT_TimeConstNotFound | PID Autotune Failed, Time Constant Not Found
67 | b_ALM_PID_AT_ProcLimitExceeded | PID Autotune Failed, Process Limit Exceeded

## EM_UOM
EUROMAP UNIT OF MEASURE (UOM)
UNIT | INDEX | COMMON CODE | ID
°F | 1 | U01 | 5582897
°C | 2 | U02 | 5582898
Δ°F | 3 | U03 | 5582899
Δ°C | 4 | U04 | 5582900
gpm | 5 | U05 | 5582901
Lpm | 6 | U06 | 5582902
milliseconds | 7 | U07 | 5582903
seconds | 8 | U08 | 5582904
minutes | 9 | U09 | 5582905
hours | 10 | U10 | 5583152
% | 11 | U11 | 5583153
gal/min/psi | 12 | U12 | 5583154
psi | 13 | U13 | 5583155
bar | 14 | U14 | 5583156
Δpsi | 15 | U15 | 5583157
Δbar | 16 | U16 | 5583158
operations | 17 | U17 | 5583159
pulses/gal | 18 | U18 | 5583160
pulses/L | 19 | U19 | 5583161
ft | 20 | U20 | 5583408
m | 21 | U21 | 5583409
V | 22 | U22 | 5583410
mA | 23 | U23 | 5583411
°F/hour | 24 | U24 | 5583412
°C/hour | 25 | U25 | 5583413
W | 26 | U26 | 5583414
kW | 27 | U27 | 5583415
events | 28 | U28 | 5583416
step | 29 | U29 | 5583417
steps | 30 | U30 | 5583663
Yes/No | 31 | U31 | 5583664
No/Yes | 32 | U32 | 5583665
operations/hr | 33 | U33 | 5583666
Δ°C<dot>sec | 34 | U34 | 5583667
Δ°F<dot>sec | 35 | U35 | 5583668
V or mA | 36 | U36 | 5583669
Ω | 37 | U37 | 5583670
Inactive/Active | 38 | U38 | 5583671
Disabled/Enabled | 39 | U39 | 5583672
Manual/Auto | 40 | U40 | 5583920
On/Off | 41 | U41 | 5583921
Off/On | 42 | U42 | 5583922
counts | 43 | U43 | 5583923

## EM_Security
EUROMAP UNIT OF MEASURE (UOM) SECURITY
CATEGORY | SECURITY | COMMENTS
COMMANDS | Read/Write
STATUS | Read-Only
PARAMS_DINT
.CurrentValue | Read-Only
.Implemented | Read-Only
.Maximum | Read-Only
.Minimum | Read-Only
.RemoteWriteAccess | Read-Only
.RemoteValue | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
PARAMS_BOOL
.CurrentValue | Read-Only
.Implemented | Read-Only
.Maximum | Read-Only
.Minimum | Read-Only
.RemoteWriteAccess | Read-Only
.RemoteValue | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
PARAMS_REAL
.CurrentValue | Read-Only
.Implemented | Read-Only
.Maximum | Read-Only
.Minimum | Read-Only
.RemoteWriteAccess | Read-Only
.RemoteValue | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
PARAMS_ANA
.CurrentValueX1 | Read-Only
.CurrentValueX2 | Read-Only
.CurrentValueY1 | Read-Only
.CurrentValueY2 | Read-Only
.Implemented | Read-Only
.MaximumX1 | Read-Only
.MaximumX2 | Read-Only
.MaximumY1 | Read-Only
.MaximumY2 | Read-Only
.MinimumX1 | Read-Only
.MinimumX2 | Read-Only
.MinimumY1 | Read-Only
.MinimumY2 | Read-Only
.RemoteWriteAccess | Read-Only
.RemoteValueX1 | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
.RemoteValueX2 | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
.RemoteValueY1 | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
.RemoteValueY2 | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
PARAMS_IPv4
.CurrentValue[1] | Read-Only
.CurrentValue[2] | Read-Only
.CurrentValue[3] | Read-Only
.CurrentValue[4] | Read-Only
.Implemented | Read-Only
.RemoteWriteAccess | Read-Only
.RemoteValue[1] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
.RemoteValue[2] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
.RemoteValue[3] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
.RemoteValue[4] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
WARNINGS
.Value | Read-Only
.Enable | Read-Only
.AutoReset | Read-Only
.Count | Read-Only
ALARMS
.Value | Read-Only
.Enable | Read-Only
.AutoReset | Read-Only
.Count | Read-Only
INPUTS_DIG
.Value | Read-Only
.Implemented | Read-Only
.Error | Read-Only
INPUTS_ANA
.Value | Read-Only
.Implemented | Read-Only
.Error | Read-Only
OUTPUTS_DIG
.Value | Read-Only
.Implemented | Read-Only
.Error | Read-Only
OUTPUTS_ANA
.Value | Read-Only
.Implemented | Read-Only
.Error | Read-Only
RAMP_SOAK
n_RampSoakMaxSteps | Read-Only
st_NET_RampSoakRecipe.InterimSetpointSts | Read-Only
st_NET_RampSoakRecipe.NextActionCountdown | Read-Only
st_NET_RampSoakRecipe.Steps[1] | Read-Only
st_NET_RampSoakRecipe.Steps[2] | Read-Only
st_NET_RampSoakRecipe.Steps[3] | Read-Only
st_NET_RampSoakRecipe.Steps[4] | Read-Only
st_NET_RampSoakRecipe.Steps[5] | Read-Only
b_RampSoakRecipe_RemWriteAccess | Read-Only
b_RampSoakRecipe_WriteRemoteData | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
st_RampSoakRecipeToSet.Steps[1] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
st_RampSoakRecipeToSet.Steps[2] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
st_RampSoakRecipeToSet.Steps[3] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
st_RampSoakRecipeToSet.Steps[4] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
st_RampSoakRecipeToSet.Steps[5] | Read/Write | If written to when .RemoteWriteAccess is FALSE, no harm will be done; value will simply revert to .CurrentValue.
DISPLAY
.Implemented | Read-Only
.Value | Read-Only
.Minimum | Read-Only
.Maximum | Read-Only
.Error | Read-Only
HEALTH
.Implemented | Read-Only
.Value | Read-Only
.Minimum | Read-Only
.Maximum | Read-Only
.Error | Read-Only
Anything with an "NR" Suffix | Read-Only
POWER
r_PumpNominalPower_W | Read-Only
r_HeaterNominalPower_W | Read-Only
r_ControlNominalPower_W | Read-Only
r_SystemNominalPower_kW | Read-Only
r_PumpPower_W | Read-Only
r_HeaterPower_W | Read-Only
r_ControlPower_W | Read-Only
r_SystemPower_kW | Read-Only
DATE_TIME
st_CurrentLocalDateTime | Read-Only
st_NET_DateTimeToSet | Read/Write
n_NET_RTC_SetClockCount | Read/Write